## Cover
#VALUE!
Wastewater net zero
| Model code: | PR24CA88
| Version number: | 1
| File name: | #VALUE!
| Date: | December 2024
| For enquiries please contact: | PR24@ofwat.gov.uk
| Sheet | Description
Inputs
| BPT inputs | Inputs from PR24 business plan data tables
Consolidated inputs
| Consolidated data | Key input data from PR24_BP required for model and assessment
| Input override | Overrides to input sheet with explanation
| Data final | Input data after overrides
Analysis
| Phase 1 - initial assessment | Written scheme level assessment
| Phase 2 - Net zero value | Written scheme level assessment
| Unit costs | Unit cost calculations
| Phase 3 | Written scheme level unit cost assessment
Outputs
| Allowances | Calculated allowances
Summary of the model:
To assess submitted schemes to the net zero challenge in company's PR24 business plan submissions in table CWW22. Following the PR24 methodology, we assessed company submissions over three phases:
1. Net zero challenge eligibility- proposed schemes were considered eligible if driven by net zero and not related to other cost drivers (e.g., overlap with base expenditure and other enhancment areas such as WINEP/NEP and IED).
2. Best value assessment- assessed ability of schemes to support sector innovation and learning, the impacts of schemes being clearly demonstrated through a proposed programme of monitoring and reporting, with the schemes forming part of a long-term delivery strategy that enables achievement of net zero. We conducted a deep dive into proposed process emissions schemes.
3. Unit ranking cost- we assessed unit cost in two ways. One, the unit rate of emission abatement delivered for each investment in AMP8. Two, the lifetime unit costs of carbon abatement.
Proposed schemes had to pass each phase of the assessment to progress through the phases. 14 schemes passed all three phases and are considered eligible for funding.
Quality assurance: This model has been subject to Ofwat internal quality assurance and has been subject to external review.
Disclaimer: This model is part of our final determinations setting out the price, service, and incentive package for water companies for the period 2025-30. It should be read together with the other documents and information that we have now published.
Changes since previous published model: N/A

## Conceptual model
#VALUE!
Conceptual model
End of sheet
Phase 1
Deep dive on process emissions (part of phase 2)
BPT inputs:
PR24 business plan data (FY25-FY30)
Allowance
Data from business plan tables was overwritten in cases where query responses indicated changes to schemes.
For all companies, allowances are not allocated by price control. Calculated allowances are profiled across AMP8 (2025-30) based on the profile of business plan submissions
F_Outputs
Phase 2
Phase 3
Data: consolidated input data
Override: input data override
Final data

## BPT input
#VALUE!
Company | Link | Date of BPT | Scheme ID | Scheme name | Scheme description | Selected or Feasible | Units | DPs | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | PR24 BP reference
[9 empty] | Scheme Capex | Scheme Opex | Scheme Totex | Scheme Capex | Scheme Opex | Scheme Totex | Scheme Capex | Scheme Opex | Scheme Totex | Scheme Capex | Scheme Opex | Scheme Totex | Scheme Capex | Scheme Opex | Scheme Totex | AMP8 Capex Total | AMP8 Opex Total | AMP8 Totex Total | Water Resources costs (% of AMP 8 Totex) | Water Network + costs (% of AMP 8 Totex) | Scheme benefits (cumulative impact on tCO2e) | Scheme benefits (cumulative impact on tCO2e) | Scheme benefits (cumulative impact on tCO2e) | Scheme benefits (cumulative impact on tCO2e) | Scheme benefits (cumulative impact on tCO2e) | Overall scheme impact on total greehouse gas emissions (total impact on tCO2e)
[9 empty] | 1: 2025-26; 4: 2026-27; 7: 2027-28; 10: 2028-29; 13: 2029-30; 16: 2025-30 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2029-30
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.1 | Cotton Valley STC - Centrate quality | Liquor recovery | Selected | £m | 3 | 0 | 0 | 0 | 0.481 | 0 | 0.481 | 3.432 | 0 | 3.432 | 6.035 | 0 | 6.035 | 4.428 | 0.191 | 4.619 | 14.376 | 0.191 | 14.567 | 100 | 0 |  |  |  |  | -191.592 | 403.376
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.2 | Cotton Valley STC gas to grid | Biogas Upgrading & Injection to Grid Rev 2 | Selected | £m | 3 | 2.254 | 0 | 2.254 | 5.259 | 0.262 | 5.521 | 0 | 0.511 | 0.511 | 0 | 0.511 | 0.511 | 0 | 0.511 | 0.511 | 7.513 | 1.796 | 9.309 | 0 | 100 |  | -854.65 | -2563.96 | -4273.25 | -5982.55 | -5542.57
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.3 | Great Billing STC gas to grid | Biogas Upgrading & Injection to Grid Rev 2 | Selected | £m | 3 | 1.621 | 0 | 1.621 | 3.782 | 0.237 | 4.019 | 0 | 0.461 | 0.461 | 0 | 0.461 | 0.461 | 0 | 0.461 | 0.461 | 5.403 | 1.62 | 7.023 | 0 | 100 |  | -3298.64 | -9895.91 | -16493.18 | -23090.45 | -22650.465
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.4 | Cotton Valley STC Fugitive emissions CH4 | Contain and treat no cake barn | Selected | £m | 3 | 0.508 | 0 | 0.508 | 3.05 | 0 | 3.05 | 1.525 | -0.003 | 1.522 | 0 | -0.006 | -0.006 | 0 | -0.006 | -0.006 | 5.083 | -0.014 | 5.069 | 0 | 100 |  |  | -787.637 | -2362.91 | -3988.18 | -3691.52
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.5 | Whitlingham STC Gas to Grid (AMP8) | Biogas Upgrading & Injection to Grid Rev 2 | Selected | £m | 3 | 2.83 | 0 | 2.83 | 6.603 | 0.21 | 6.813 | 0 | 0.409 | 0.409 | 0 | 0.409 | 0.409 | 0 | 0.409 | 0.409 | 9.433 | 1.437 | 10.869 | 0 | 100 |  | -1201.18 | -3603.54 | -6005.9 | -8408.26 | -7968.28
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.6 | Great Billing STC Fugitive emissions CH4 | Contain and treat no cake barn | Selected | £m | 3 | 0.366 | 0 | 0.366 | 2.194 | 0 | 2.194 | 1.097 | -0.148 | 0.949 | 0 | -0.297 | -0.297 | 0 | -0.297 | -0.297 | 3.656 | -0.741 | 2.915 | 0 | 100 |  |  | -1222.7 | -3668.09 | -6113.48 | -6055.543
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.7 | Whitlingham STC Fugitive emissions CH4 | Contain and treat no cake barn | Selected | £m | 3 | 0.243 | 0 | 0.243 | 1.455 | 0 | 1.455 | 0.728 | -0.07 | 0.658 | 0 | -0.139 | -0.139 | 0 | -0.139 | -0.139 | 2.426 | -0.348 | 2.078 | 0 | 100 |  |  | -833.831 | -2501.49 | -4169.15 | -4134.595
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.8 | Cliff Quay STC Fugitive Emissions CH4 | Contain and treat no cake barn | Selected | £m | 3 | 0.405 | 0 | 0.405 | 2.429 | 0 | 2.429 | 1.214 | -0.034 | 1.181 | 0 | -0.067 | -0.067 | 0 | -0.067 | -0.067 | 4.048 | -0.168 | 3.88 | 0 | 100 |  |  | -504.698 | -1514.1 | -2523.49 | -2393.382
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.9 | Pyewipe STC Fugitive emissions CH4 | Contain and treat no cake barn | Selected | £m | 3 | 0.406 | 0 | 0.406 | 2.438 | 0 | 2.438 | 1.219 | -0.05 | 1.169 | 0 | -0.1 | -0.1 | 0 | -0.1 | -0.1 | 4.063 | -0.25 | 3.813 | 0 | 100 |  |  | -609.5 | -1828.5 | -3047.5 | -2909.58
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.10 | Colchester STC Fugitive emissions CH4 | Contain and treat no cake barn | Selected | £m | 3 | 0.369 | 0 | 0.369 | 2.213 | 0 | 2.213 | 1.107 | -0.033 | 1.073 | 0 | -0.066 | -0.066 | 0 | -0.066 | -0.066 | 3.689 | -0.166 | 3.523 | 0 | 100 |  |  | -506.359 | -1519.08 | -2531.79 | -2407.401
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.11 | Basildon STC Fugitive emissions CH4 | Contain and treat no cake barn | Selected | £m | 3 | 0.41 | 0 | 0.41 | 2.461 | 0 | 2.461 | 1.23 | -0.011 | 1.22 | 0 | -0.022 | -0.022 | 0 | -0.022 | -0.022 | 4.101 | -0.054 | 4.047 | 0 | 100 |  |  | -17.787 | -56.36 | -88.933 | 56.021
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.12 | Kings Lynn STC Fugitive emissions CH4 | Contain and treat no cake barn | Selected | £m | 3 | 0.41 | 0 | 0.41 | 2.459 | 0 | 2.459 | 1.229 | -0.044 | 1.186 | 0 | -0.087 | -0.087 | 0 | -0.087 | -0.087 | 4.098 | -0.218 | 3.881 | 0 | 100 |  |  | -633.196 | -1899.59 | -3165.98 | -3021.87
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.13 | Cotton Valley WRC Fugitive emissions CH4 | Contain and treat | Selected | £m | 3 | 0.015 | 0 | 0.015 | 0.092 | 0 | 0.092 | 0.046 | 0 | 0.046 | 0 | 0 | 0 | 0 | 0 | 0 | 0.154 | 0 | 0.154 | 100 | 0 |  |  | -24.36 | -73.08 | -121.8 | -114.569
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.14 | Basildon STC Fugitive emissions N2O | Contain and treat | Selected | £m | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.305 | 0 | 0.305 | 0.715 | 0 | 0.715 | 0.528 | 0.014 | 0.542 | 1.548 | 0.014 | 1.562 | 100 | 0 |  |  |  |  | -174 | -107.799
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.15 | Colchester STC Fugitive emissions N2O | Contain and treat Anoxic/Aeration only | Selected | £m | 3 | 0.287 | 0 | 0.287 | 0.573 | 0 | 0.573 | 0.573 | 0.014 | 0.587 | 0 | 0.027 | 0.027 | 0 | 0.027 | 0.027 | 1.433 | 0.068 | 1.5 | 100 | 0 |  |  | -116 | -348 | -580 | -521.085
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.16 | Cliff Quay STC Fugitive emissions N2O | Contain and treat Anoxic/Aeration only | Selected | £m | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.318 | 0 | 0.318 | 0.637 | 0 | 0.637 | 0.637 | 0.014 | 0.651 | 1.592 | 0.014 | 1.606 | 100 | 0 |  |  |  |  | -273 | -193.664
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.17 | Whitlingham STC Fugitive Emissions N2O | Contain and treat | Selected | £m | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.138 | 0 | 0.138 | 0.277 | 0 | 0.277 | 0.277 | 0.012 | 0.289 | 0.692 | 0.012 | 0.704 | 100 | 0 |  |  |  |  | -215 | -203.747
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.18 | Cotton Valley WRC Fugitive emissions N2O | Anoxic extension and RTC | Selected | £m | 3 | 0.499 | 0 | 0.499 | 1.407 | 0 | 1.407 | 2.313 | 0.006 | 2.319 | 1.427 | 0.077 | 1.504 | 0 | 0.141 | 0.141 | 5.647 | 0.224 | 5.871 | 100 | 0 |  |  | -24.648 | -357.396 | -973.596 | -696.171
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.19 | Great Billing WRC Fugitive Emissions N2O | Enhanced aeration and RTC | Selected | £m | 3 | 0 | 0 | 0 | 0.827 | 0 | 0.827 | 2.343 | 0 | 2.343 | 4.264 | 0 | 4.264 | 3.112 | 0 | 3.112 | 10.546 | 0 | 10.546 | 100 | 0 |  |  |  |  | -540.5 | -419.599
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.20 | Basildon WRC Fugitive Emissions N2O | Anoxic extension and RTC | Selected | £m | 3 | 0 | 0 | 0 | 0.157 | 0 | 0.157 | 0.659 | 0 | 0.659 | 1.147 | 0 | 1.147 | 0.809 | 0.005 | 0.814 | 2.773 | 0.005 | 2.778 | 100 | 0 |  |  |  |  | -341.4 | -310.212
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.21 | Bedford WRC Fugitive Emissions N2O | Diffuser upgrade and RTC | Selected | £m | 3 | 0 | 0 | 0 | 0.028 | 0 | 0.028 | 0.281 | 0 | 0.281 | 0.48 | 0 | 0.48 | 0.343 | 0 | 0.343 | 1.133 | 0 | 1.133 | 100 | 0 |  |  |  |  | -365.8 | -324.313
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.22 | Kings Lynn WRC Fugitive Emissions N2O | Real time N2O control | Selected | £m | 3 | 0.19 | 0 | 0.19 | 0.381 | 0 | 0.381 | 0.381 | 0 | 0.381 | 0 | 0 | 0 | 0 | 0 | 0 | 0.952 | 0 | 0.952 | 100 | 0 |  |  |  |  | -88.6 | -85.098
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.23 | Newton Marsh WRC Fugitive Emissions N2O | Real time N2O control | Selected | £m | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.089 | 0 | 0.089 | 0.179 | 0 | 0.179 | 0.179 | 0 | 0.179 | 0.447 | 0 | 0.447 | 100 | 0 |  |  |  |  | -72.5 | -71.167
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.24 | Broadholme WRC Fugitive Emissions N2O | RTC and Diffuser upgrade ASP only | Selected | £m | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.145 | 0 | 0.145 | 0.291 | 0 | 0.291 | 0.291 | 0 | 0.291 | 0.727 | 0 | 0.727 | 100 | 0 |  |  |  |  | -181.1 | -154.452
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.25 | Letchworth WRC Fugitive emissions N2O | MABR, Aeration mods and RTC | Selected | £m | 3 | 0 | 0 | 0 | 0.889 | 0 | 0.889 | 2.519 | 0 | 2.519 | 4.586 | 0 | 4.586 | 3.347 | 0.014 | 3.36 | 11.341 | 0.014 | 11.355 | 100 | 0 |  |  |  |  | -127.6 | -21.997
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.26 | Newmarket WRC Fugitive Emissions N2O | MABR and RTC | Selected | £m | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.919 | 0 | 0.919 | 1.839 | 0 | 1.839 | 1.839 | 0.011 | 1.85 | 4.597 | 0.011 | 4.608 | 100 | 0 |  |  |  |  | -26.5 | 39.302
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.27 | Hitchin WRC Fugitive emissions N2O | Anoxic extension and RTC | Selected | £m | 3 | 0 | 0 | 0 | 0.046 | 0 | 0.046 | 0.326 | 0 | 0.326 | 0.56 | 0 | 0.56 | 0.399 | 0.071 | 0.47 | 1.331 | 0.071 | 1.402 | 100 | 0 |  |  |  |  | -32.95 | 6.285
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.28 | Dunstable WRC Fugitive Emissions N2O | MABR, enhanced Aeration and RTC | Selected | £m | 3 | 0 | 0 | 0 | 0.96 | 0 | 0.96 | 2.72 | 0 | 2.72 | 4.951 | 0 | 4.951 | 3.613 | 0.057 | 3.67 | 12.244 | 0.057 | 12.301 | 100 | 0 |  |  |  |  | -75.3 | 64.152
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.29 | Flitwick WRC Fugitive Emissions N2O | MABR, enhanced Aeration and RTC | Selected | £m | 3 | 0.527 | 0 | 0.527 | 1.468 | 0 | 1.468 | 2.568 | 0.005 | 2.573 | 1.706 | 0.063 | 1.769 | 0 | 0.116 | 0.116 | 6.27 | 0.183 | 6.453 | 100 | 0 |  |  | -3.532 | -51.214 | -139.514 | -85.98
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.30 | Great Billing STC Liquor Ammonia | Centrate treatment plant | Selected | £m | 3 | 0 | 0 | 0 | 0.239 | 0 | 0.239 | 1.705 | 0 | 1.705 | 2.924 | 0 | 2.924 | 2.078 | 0.433 | 2.511 | 6.946 | 0.433 | 7.379 | 100 | 0 |  |  |  |  | -557 | 26.487
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.31 | Logistics Fleet CO2 emissions 2025-26 | Electrification of HGVs 2025-26 | Selected | £m | 3 | 1.352 | -0.239 | 1.114 | 0 | -0.239 | -0.239 | 0 | -0.239 | -0.239 | 0 | -0.239 | -0.239 | 0 | -0.239 | -0.239 | 1.352 | -1.194 | 0.159 | 0 | 100 | -770.646 | -1514.292 | -2311.938 | -3082.584 | -3853.23 | -3853.23
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.32 | Logistics fleet CO2 emissions 2026-27 | Electrification of HGVs | Selected | £m | 3 | 0 | 0 | 0 | 1.62 | -0.187 | 1.433 | 0 | -0.187 | -0.187 | 0 | -0.187 | -0.187 | 0 | -0.187 | -0.187 | 1.62 | -0.747 | 0.873 | 0 | 100 |  | -577.988 | -1155.976 | -1733.964 | -2311.952 | -2311.952
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.33 | Logistics fleet CO2 emissions 2027-28 | Electrification of HGVs | Selected | £m | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 2.054 | -0.249 | 1.805 | 0 | -0.249 | -0.249 | 0 | -0.249 | -0.249 | 2.054 | -0.747 | 1.307 | 0 | 100 |  |  | -770.616 | -1514.292 | -2311.938 | -2311.848
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.34 | Logistics fleet CO2 emissions 2028-29 | Electrification of HGVs | Selected | £m | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.789 | -0.217 | 1.573 | 0 | -0.217 | -0.217 | 1.789 | -0.433 | 1.356 | 0 | 100 |  |  |  | -674.286 | -1348.572 | -1348.572
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.35 | Logistics fleet CO2 emissions 2029-30 | Electrification of HGVs | Selected | £m | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.51 | -0.588 | 3.922 | 4.51 | -0.588 | 3.922 | 0 | 100 |  |  |  |  | -1830.29 | -1830.285
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.36 | Huntingdon WRC Fugitive Emissions N2O | Aeration upgrade and RTC | Selected | £m | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91 | 0 | 0.91 | 1.881 | 0 | 1.881 | 2.791 | 0 | 2.791 | 100 | 0 |  |  |  |  | -87.3 | -67.237
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.37 | AMP8 Small Scale Solar Delivery WR | WR Mounted Panels | Feasible | £m | 3 | 2.017 | 0 | 2.017 | 2.017 | -0.24 | 1.777 | 2.017 | -0.481 | 1.536 | 2.017 | -0.721 | 1.296 | 2.017 | -0.962 | 1.055 | 10.085 | -2.404 | 7.681 | 100 |  |  | -454.48 | -1363.74 | -2727.48 | -4545.8 | -3045.8
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.38 | Basildon STC Gas to Grid | Biogas Upgrading & Injection to Grid Rev 2 | Feasible | £m | 3 | 1.5 | 0 | 1.5 | 3.376 | 0 | 3.376 | 3.352 | 0 | 3.352 | 0.686 | 1.751 | 2.437 | 0 | 2.101 | 2.101 | 8.914 | 3.852 | 12.766 |  | 100 |  |  |  | -1088.74 | -2177.48 | -1909.86
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.39 | Colchester STC Gas to Grid | Biogas Upgrading & Injection to Grid Rev 2 | Feasible | £m | 3 | 1.5 | 0 | 1.5 | 3.376 | 0 | 3.376 | 3.352 | 0 | 3.352 | 0.686 | 2.461 | 3.147 | 0 | 2.953 | 2.953 | 8.914 | 5.414 | 14.328 |  | 100 |  |  |  | -1324.84 | -2649.68 | -2382.06
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.40 | Ipswich Cliff Quay STC Gas to Grid | Biogas Upgrading & Injection to Grid Rev 2 | Feasible | £m | 3 | 1.5 | 0 | 1.5 | 3.376 | 0 | 3.376 | 3.352 | 0 | 3.352 | 0.686 | 2.352 | 3.038 | 0 | 2.822 | 2.822 | 8.914 | 5.174 | 14.088 |  | 100 |  |  |  | -1692.08 | -3384.16 | -3116.54
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.41 | Pyewipe STC Gas to Grid | Biogas Upgrading & Injection to Grid Rev 2 | Feasible | £m | 3 | 1.5 | 0 | 1.5 | 3.376 | 0 | 3.376 | 3.352 | 0 | 3.352 | 0.686 | 2.387 | 3.073 | 0 | 2.864 | 2.864 | 8.914 | 5.251 | 14.165 |  | 100 |  |  |  | -3361 | -6722 | -6454.38
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.42 | Kings Lynn STC gas to grid | Biogas Upgrading & Injection to Grid Rev 2 | Feasible | £m | 3 | 1.5 | 0 | 1.5 | 3.376 | 0 | 3.376 | 3.352 | 0 | 3.352 | 0.686 | 2.617 | 3.303 | 0 | 3.141 | 3.141 | 8.914 | 5.758 | 14.672 |  | 100 |  |  |  | -3360 | -6720 | -6452.38
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.43 | Whitlingham WRC Fugitive Emissions N2O | Real time N2O control. | Feasible | £m | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.967 | 0 | 0.967 | 0 | 0 | 0 | 0.967 | 0 | 0.967 | 100 | [5 empty] | -418.8 | -415.39
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.44 | Colchester WRC Fugitive Emissions N2O | Real time N2O control | Feasible | £m | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.831 | 0 | 0.831 | 0.831 | 0 | 0.831 | 0 | 0 | 0 | 1.662 | 0 | 1.662 | 100 | [5 empty] | -192.5 | -189.6
ANH | v6.11 Data tables ANH resubmission 25.01.24.xlsb (sharepoint.com) | 2024-01-25 | CWW22.45 | Colchester WRC Fugitive Emissions N2O | MABR and RTC | Feasible | £m | 3 | 3.121 | 0 | 3.121 | 7.282 | 0 | 7.282 | 0 | 0.021 | 0.021 | 0 | 0.021 | 0.021 | 0 | 0.021 | 0.021 | 10.403 | 0.063 | 10.466 | 100 |  |  |  | -264.7 | -529.4 | -794.1 | -791.2
HDD | (Post Submission) HDD16_150224 Data Tables.xlsb (sharepoint.com) | 2024-02-15 | CWW22.1 | Process Emissions Reduction | Digital twin & ASP Cover & Treat to reduce N2O production - Included in our Net Zero Challenge Fund Investment Case | Select from Dropdown | £m | 3 | 0.491 |  | 0.491 | 0.296 |  | 0.296 |  | 0.025 | 0.025 |  | 0.025 | 0.025 |  | 0.025 | 0.025 | 0.787 | 0.076 | 0.864 | 100 |  |  |  | -137.13 | -274.265 | -411.398 | -404.104
HDD | (Post Submission) HDD16_150224 Data Tables.xlsb (sharepoint.com) | 2024-02-15 | CWW22.2 | Heat Decarbonisation | Replacement of fossil fuel boilers with heat pumps for space heating - Included in our Net Zero Challenge Fund Investment Case | Select from Dropdown | £m | 3 | 1: 0.038; 3: 0.038; 6: 0; 9: 0; 12: 0; 15: 0; 16: 0.038; 17: 0; 18: 0.038; 19: 100 |  | -5.473 | -10.947 | -16.42 | -21.893 | -21.033
SVE | (Post Submission) SVE40_150224 Data Tables.xlsb (sharepoint.com) | 2024-02-15 | NZ#1 | Digital Twin | Digital twin to reduce N2O production - Included in our Net Zero Challenge Fund Investment Case | Selected | £m | 3 | 12.786 | 0 | 12.786 | 25.571 | 0 | 25.571 | 0 | -2.118 | -2.118 | 12.786 | -4.235 | 8.551 | 12.786 | -4.235 | 8.551 | 63.929 | -10.588 | 53.341 | 100 | 0 | 0 | 0 | -5939.59 | -17818.77 | -35637.54 | -35617.956
SVE | (Post Submission) SVE40_150224 Data Tables.xlsb (sharepoint.com) | 2024-02-15 | NZ#2 | Cover & Treat | Cover ASP reactors and liquor treatment plants and treat to remove N2O - Included in our Net Zero Challenge Fund Investment Case | Selected | £m | 3 | 18.579 | 0 | 18.579 | 18.579 | 0 | 18.579 | 18.579 | 0 | 18.579 | 18.579 | 0 | 18.579 | 18.579 | 0 | 18.579 | 92.895 | 0 | 92.895 | 98.268 | 1.732 | 0 | 0 | -7607.71 | -23251.86 | -74239.11 | -71747.88
SVE | (Post Submission) SVE40_150224 Data Tables.xlsb (sharepoint.com) | 2024-02-15 | NZ#3 | ASP Intensification | ASP intensification to reduce N2O production - Included in our Net Zero Challenge Fund Investment Case | Selected | £m | 3 | 4.076 | 0 | 4.076 | 28.561 | 0 | 28.561 | 25.891 | 0 | 25.891 | 23.954 | 0 | 23.954 | 21.629 | 0 | 21.629 | 104.111 | 0 | 104.111 | 100 | 0 | 0 | 0 | -8326.56 | -24979.68 | -49959.36 | -44255
SVE | (Post Submission) SVE40_150224 Data Tables.xlsb (sharepoint.com) | 2024-02-15 | NZ#4 | Active gas capture | Active gas capture around digestion to reduce CH4 production - Included in our Net Zero Challenge Fund Investment Case | Selected | £m | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 33.179 | 0 | 33.179 | 22.33 | 0 | 22.33 | 35.77 | 0 | 35.77 | 91.279 | 0 | 91.279 | 0 | 100 | 0 | 0 | -8013.61 | -24040.83 | -48081.66 | -46459.67
SVE | (Post Submission) SVE40_150224 Data Tables.xlsb (sharepoint.com) | 2024-02-15 | NZ#5 | EV Charging Infrastructure | EV charge points - Included in our Net Zero Challenge Fund Investment Case | Selected | £m | 3 | 0 | 0 | 0 | 0.72 | 0 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72 | 0 | 0.72 | 42.222 | 57.778 | 0 | 0 | -311.4 | -934.2 | -1868.4 | -1850.81
SVE | (Post Submission) SVE40_150224 Data Tables.xlsb (sharepoint.com) | 2024-02-15 | NZ#6 | Heat pumps | Replacement of fossil fuel boilers with heat pumps for space heating - Included in our Net Zero Challenge Fund Investment Case | Selected | £m | 3 | 6.598 | 0 | 6.598 | 0 | 0 | 0 | 0 | -0.06 | -0.06 | 0 | -0.09 | -0.09 | 0 | -0.09 | -0.09 | 6.598 | -0.24 | 6.358 | 42.222 | 57.778 | 0 | 0 | -209.25 | -627.75 | -1255.5 | -1171.69
SVE | (Post Submission) SVE40_150224 Data Tables.xlsb (sharepoint.com) | 2024-02-15 | NZ#7 | HVO diesel replacement | Infrastructure to enable replacement of mineral diesel with HVO - Included in our Net Zero Challenge Fund Investment Case | Selected | £m | 3 | 0.271 | 0 | 0.271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.271 | 0 | 0.271 | 42.222 | 57.778 | 0 | 0 | -567 | -1701 | -3402 | -2034
SVE | (Post Submission) SVE40_150224 Data Tables.xlsb (sharepoint.com) | 2024-02-15 | NZ#8 | Cellulose recovery | Recovery of cellulose to use in biomass boilers to replace natural gas - Included in our Net Zero Challenge Fund Investment Case | Selected | £m | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 31.772 | 0 | 31.772 | 31.772 | 0 | 31.772 | 0 | -0.469 | -0.469 | 63.544 | -0.469 | 63.075 | 0 | 100 | 0 | 0 | -1516.8 | -7810.4 | -15620.8 | -15571.3
SVE | (Post Submission) SVE40_150224 Data Tables.xlsb (sharepoint.com) | 2024-02-15 | NZ#9 | Process Optimisation | Instrumentation & optimisation to reduce N2O production - Included in our Net Zero Challenge Fund Investment Case | Selected | £m | 3 | 6.045 | 0 | 6.045 | 0 | 0 | 0 | 0 | 0.738 | 0.738 | 0 | 1.092 | 1.092 | 0 | 1.092 | 1.092 | 6.045 | 2.922 | 8.967 | 100 | 0 | 0 | 0 | -34000 | -68000 | -102000 | -101959.2
SVE | (Post Submission) SVE40_150224 Data Tables.xlsb (sharepoint.com) | 2024-02-15 | NZ#10 | Hydrogen Production | Production of hydrogen by electrolysis of high strength liquors - Not included in our Investment Cases, we consider this to be base expenditure if economic. | Feasible | £m | 3 | 0.45 | 0 | 0.45 | 0.45 | 0 | 0.45 | 0.45 | -0.213 | 0.237 | 0.45 | -0.213 | 0.237 | 0.45 | -0.213 | 0.237 | 2.25 | -0.639 | 1.611 | 42.222 | 57.778 | 0 | 0 | -806.4 | -1612.8 | -2419.2 | -2226.255
SVE | (Post Submission) SVE40_150224 Data Tables.xlsb (sharepoint.com) | 2024-02-15 | NZ#11 | Electrical storage | Behind the meter battery storage - Not included in our Investment Cases, we consider this to be base expenditure if economic. | Feasible | £m | 3 | 0.99 | 0 | 0.99 | 0.99 | 0 | 0.99 | 0.99 | -0.413 | 0.577 | 0.99 | -0.413 | 0.577 | 0.99 | -0.413 | 0.577 | 4.95 | -1.239 | 3.711 | 42.222 | 57.778 | 0 | 0 | -32.85 | -65.7 | -98.55 | 325.928
SVE | (Post Submission) SVE40_150224 Data Tables.xlsb (sharepoint.com) | 2024-02-15 | NZ#12 | EV fleet only | EV vehicles - Not included in our Investment Cases, we consider vehicle replacement to be part of base expenditure but note that there is a cost premium for electric vehicles. | Feasible | £m | 3 | 0.657 | 0 | 0.657 | 0.657 | 0 | 0.657 | 0.657 | 0 | 0.657 | 0.657 | 0 | 0.657 | 0.657 | 0 | 0.657 | 3.285 | 0 | 3.285 | 42.222 | 57.778 | 0 | 0 | -1557 | -3114 | -4671 | -4389.301
SVE | (Post Submission) SVE40_150224 Data Tables.xlsb (sharepoint.com) | 2024-02-15 | NZ#13 | HVO fuel only | HVO (marginal cost of fuel only) - Not included in our Investment Cases, we consider this to be base expenditure but note that there is a cost premium for HVO fuel. | Feasible | £m | 3 | 0 | 0.36 | 0.36 | 0 | 0.36 | 0.36 | 0 | 0.36 | 0.36 | 0 | 0.36 | 0.36 | 0 | 0.36 | 0.36 | 0 | 1.8 | 1.8 | 42.222 | 57.778 | -2271.6 | -4543.2 | -6814.8 | -9086.4 | -11358 | -11203.64
SVE | (Post Submission) SVE40_150224 Data Tables.xlsb (sharepoint.com) | 2024-02-15 | NZ#14 | Solar PV | Solar PV (other than very small scale) - Not included in our Investment Cases, we consider this to be base expenditure if economic. | Feasible | £m | 3 | 2.34 | 0 | 2.34 | 2.34 | 0 | 2.34 | 2.34 | -2.625 | -0.285 | 2.34 | -2.625 | -0.285 | 2.34 | -2.625 | -0.285 | 11.7 | -7.875 | 3.825 | 42.222 | 57.778 | 0 | 0 | -2625.37 | -5250.74 | -7876.12 | -6872.8
TMS | TMS55 PR24 Data Tables submitted 081223.xlsb (sharepoint.com) | 2023-12-08 | CWW22_1 | S40749/1 (Long Reach - Installation of Biomethane Plant - Delta from botex for bidding process) | Biomethane plant | Feasible | £m | 3 | 5.886 | 0 | 5.886 | 0 | 3.747 | 3.747 | 0 | 2.985 | 2.985 | 0 | 3.018 | 3.018 | 0 | 3.186 | 3.186 | 5.886 | 12.936 | 18.822 | 0% | 100% | 0 | 0 | -2537.57 | -5075.14 | -7612.71 | -5547.48
TMS | TMS55 PR24 Data Tables submitted 081223.xlsb (sharepoint.com) | 2023-12-08 | CWW22_2 | Aylesbury - Installation of Biomethane Plant with heat pump - Delta from botex for bidding process | Biomethane plant | Feasible | £m | 3 | 0 | 0 | 0 | 1.107 | 0 | 1.107 | 0.371 | 0 | 0.371 | 0 | 0.472 | 0.472 | 0 | 0.5 | 0.5 | 1.478 | 0.972 | 2.45 | 0% | 100% | 0 | 0 | 0 | -476.348 | -952.697 | -253.827
TMS | TMS55 PR24 Data Tables submitted 081223.xlsb (sharepoint.com) | 2023-12-08 | CWW22_3 | Bishop Stortford - Installation of Biomethane Plant - enhancement from botex for bidding process | Biomethane plant | Feasible | £m | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.355 | 0.355 | 0 | 0.258 | 0.258 | 0 | 0.613 | 0.613 | 0% | 100% | 0 | 0 | 0 | -290.137 | -581.009 | -701.799
TMS | TMS55 PR24 Data Tables submitted 081223.xlsb (sharepoint.com) | 2023-12-08 | CWW22_4 | Didcot - Installation of Biomethane Plant - enhancement from botex for bidding process | Biomethane plant | Feasible | £m | 3 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0.112 | 0.112 | 0 | 0.115 | 0.115 | 0 | 0.126 | 0.126 | 0 | 0.453 | 0.453 | 0% | 100% | 0 | -369.425 | -677.409 | -985.392 | -1293.376 | -1699.066
TMS | TMS55 PR24 Data Tables submitted 081223.xlsb (sharepoint.com) | 2023-12-08 | CWW22_5 | East Hyde - Installation of Biomethane Plant - enhancement from botex for bidding process | Biomethane plant | Feasible | £m | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.519 | 0.519 | 0 | 0.555 | 0.555 | 0 | 1.074 | 1.074 | 0% | 100% | 0 | 0 | 0 | -558.252 | -1116.504 | -208.614
TMS | TMS55 PR24 Data Tables submitted 081223.xlsb (sharepoint.com) | 2023-12-08 | CWW22_6 | Hogsmill -Installation of Biomethane Plant - enhancement from botex for bidding process | Biomethane plant | Feasible | £m | 3 | 0 | 0 | 0 | 1.777 | 0 | 1.777 | 1.185 | 0 | 1.185 | 0 | 1.239 | 1.239 | 0 | 1.303 | 1.303 | 2.962 | 2.542 | 5.504 | 0% | 100% | 0 | 0 | 0 | -1109.173 | -2219.814 | 727.656
TMS | TMS55 PR24 Data Tables submitted 081223.xlsb (sharepoint.com) | 2023-12-08 | CWW22_7 | Reading - Installation of Biomethane Plant - enhancement from botex for bidding process | Biomethane plant | Feasible | £m | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.923 | 0.923 | 0 | 1.044 | 1.044 | 0 | 1.967 | 1.967 | 0% | 100% | 0 | 0 | 0 | -1040.033 | -2138.606 | -912.736
TMS | TMS55 PR24 Data Tables submitted 081223.xlsb (sharepoint.com) | 2023-12-08 | CWW22_8 | S40040/4 (PR24 Fleet - Life expired Enhancement (cost to convert to electrical) (Waste)) | Costs above base of converting life-expired transport to electric or alternative fuelled vehicle. | Feasible | £m | 3 | 7.279 | -0.562 | 6.717 | 6.627 | -0.599 | 6.028 | 5.369 | -0.642 | 4.727 | 3.912 | -0.713 | 3.199 | 1.152 | -1.013 | 0.139 | 24.339 | -3.529 | 20.81 | 83% | 17% | -1212 | -3150 | -5770 | -9140 | -13142 | 2067
TMS | TMS55 PR24 Data Tables submitted 081223.xlsb (sharepoint.com) | 2023-12-08 | CWW22_9 | S40841/1 (PR24 Hybrid air source heat pump/existing boiler for 4 corporate offices (Waste)) | Lower GHG emission hybrid heating at four corporate offices | Feasible | £m | 3 | 0.609 | -0.004 | 0.605 | 0.611 | -0.082 | 0.529 | 0 | -0.054 | -0.054 | 0 | -0.037 | -0.037 | 0 | -0.025 | -0.025 | 1.22 | -0.202 | 1.018 | 100% | 0% | -198.77 | -596.3 | -993.83 | -1391.36 | -1788.89 | -1609.89
TMS | TMS55 PR24 Data Tables submitted 081223.xlsb (sharepoint.com) | 2023-12-08 | CWW22_10 | S40842/2 (PR24 Air source heat pump for site office (enhancement cost) (Waste)) | Lower GHG emission heating for life-expired site office boilers | Feasible | £m | 3 | 0.501 | 0.005 | 0.506 | 0.503 | 0.022 | 0.525 | 0.505 | 0.041 | 0.546 | 0.507 | 0.06 | 0.567 | 0.51 | 0.081 | 0.591 | 2.526 | 0.209 | 2.735 | 100% | 0% | -50 | -150.019 | -300.038 | -500.067 | -750.066 | -362.516
NWT | UUW93_OFW-OBQ-UUW-152 190224.xlsb (sharepoint.com) | 2024-02-19 | E00001337 | Stationary fossil fuel reductions | Reducing fossil fuel use in our treatment operations by replacing with low/zero carbon fuels. | Selected | £m | 3 | 6.504 | 2.568 | 9.073 | 0 | 1.453 | 1.453 | 0 | 0.439 | 0.439 | 0 | 0.977 | 0.977 | 0 | 0.819 | 0.819 | 6.504 | 6.256 | 12.761 | 0 | 1 | -7055.38 | -14110.76 | -21166.14 | -28221.52 | -35276.9 | -35249.92
NWT | UUW93_OFW-OBQ-UUW-152 190224.xlsb (sharepoint.com) | 2024-02-19 | E00001338 | Process emissions (Bioresources) | This net zero enhancement provides a major reduction in fugitive methane releases. The proposal is to use new technology to extract more biogas from the sludge which would have otherwise be lost to atmosphere. | Selected | £m | 3 | 7.293 | 0 | 7.293 | 7.409 | 0 | 7.409 | 0 | -0.287 | -0.287 | 0 | -0.325 | -0.325 | 0 | -0.314 | -0.314 | 14.702 | -0.926 | 13.776 | 0 | 1 | 0 | 0 | -7358.919 | -14717.838 | -22076.757 | -21528.347
NWT | UUW93_OFW-OBQ-UUW-152 190224.xlsb (sharepoint.com) | 2024-02-19 | E00001339 | Process emissions (Wastewater) | Sector leading nitrous oxide (N2O) emissions reduction programme | Selected | £m | 3 | 25.683 | 1.537 | 27.22 | 0.134 | 1.564 | 1.698 | 0.161 | 1.552 | 1.713 | 0.135 | 1.576 | 1.712 | 0.189 | 1.572 | 1.76 | 26.303 | 7.802 | 34.104 | 1 | 0 | 0 | 0 | -12541.041 | -37623.123 | -62705.206 | -62675.206
NWT | UUW93_OFW-OBQ-UUW-152 190224.xlsb (sharepoint.com) | 2024-02-19 | E00001340 | Transport fossil fuel reductions - Green fleet LCVs phase 1 | Procuring zero emission (Electric Vehicle, EV) cars & vans | Selected | £m | 3 | 1.68 | -0.137 | 1.543 | 2.135 | -0.532 | 1.603 | 4.239 | -1.171 | 3.068 | 3.65 | -1.839 | 1.811 | 0 | -2.217 | -2.217 | 11.704 | -5.896 | 5.808 | 0.32 | 0.329 | -337.89 | -1436.031 | -3801.258 | -7727.535 | -12370.138 | -12370.138
NWT | UUW93_OFW-OBQ-UUW-152 190224.xlsb (sharepoint.com) | 2024-02-19 | E00001341 | Transport fossil fuel reductions - Green fleet LCVs phase 2 | Procuring zero emission (Electric Vehicle, EV) cars & vans | Selected | £m | 3 | 1.976 | -0.047 | 1.928 | 2.511 | -0.184 | 2.327 | 4.985 | -0.405 | 4.58 | 4.292 | -0.636 | 3.656 | 0 | -0.766 | -0.766 | 13.764 | -2.039 | 11.725 | 0.32 | 0.329 | -116.822 | -496.493 | -1314.245 | -2671.714 | -4276.845 | -4276.845
NWT | UUW93_OFW-OBQ-UUW-152 190224.xlsb (sharepoint.com) | 2024-02-19 | E00001342 | Transport fossil fuel reductions - Green fleet Biomethane HGVs | Switching to biofuel for Bioresources HGV's. | Selected | £m | 3 | 0.307 | -0.013 | 0.294 | 0.312 | -0.04 | 0.272 | 0.31 | -0.066 | 0.244 | 0.314 | -0.094 | 0.221 | 0.313 | -0.12 | 0.193 | 1.558 | -0.333 | 1.224 | 0 | 1 | -154.634 | -618.538 | -1391.71 | -2474.152 | -3865.862 | -3865.862
NWT | UUW93_OFW-OBQ-UUW-152 190224.xlsb (sharepoint.com) | 2024-02-19 | E00001426 | Phase 2 – Further low regrets emissions reductions in AMP8 | A selection of projects with GHG emissions as the primary driver for consideration within AMP8. Due to the uncertainty and rapid evolution within the market the potential cases within our proposed phase 2 require further investigation and will be defined within AMP8. | Selected | £m | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 20.051 | 0 | 20.051 | 20.357 | 0 | 20.357 | 20.293 | 0 | 20.293 | 60.701 | 0 | 60.701 | 0.318 | 0.407 | 0 | 0 | -13229.009 | -26458.018 | -39687.026 | -38814.813
NWT | UUW93_OFW-OBQ-UUW-152 190224.xlsb (sharepoint.com) | 2024-02-19 | E00001346 | Property emissions reductions | Decarbonising heat within our UUW owned property portfolio, focused at moving away from fossil fuel usage. | Selected | £m | 3 | 2.411 | 0 | 2.411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.411 | 0 | 2.411 | 0.333 | 0.333 | -816.324 | -1632.648 | -2448.972 | -3265.296 | -4081.62 | -3987.629
NWT | UUW93_OFW-OBQ-UUW-152 190224.xlsb (sharepoint.com) | 2024-02-19 | E00001425 | Net zero catchment strategy | Development of a net zero catchment strategy for St Cuthbert's garden village development to support the new WwTw in Carlisle, facilitating the expected population growth | Selected | £m | 3 | 0.504 | 0 | 0.504 | 0.256 | 0 | 0.256 | 0.153 | 0 | 0.153 | 0.103 | 0 | 0.103 | 0 | 0 | 0 | 1.016 | 0 | 1.016 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WSH | WSH201-Additional BP Tables 240209.xlsx (sharepoint.com) | 2024-02-09 | CWW22_1 | Net Zero Carbon Strategy: Network Control Systems (Wastewater) | Delivery of a new Network Control System for Wastewater to reduce energy consumption by using factors such as weather and demand patterns to predict optimum set points, and as a result, control and optimise pumping regimes | Selected | £m | 3 | 0.174 | -0.042 | 0.132 | 0.394 | -0.097 | 0.297 | 0.394 | -0.097 | 0.297 | 0.414 | -0.101 | 0.313 | 0.349 | -0.084 | 0.265 | 1.725 | -0.421 | 1.304 | 100 | 0 | -50 | -165 | -285 | -400 | -500 | -360
WSH | WSH201-Additional BP Tables 240209.xlsx (sharepoint.com) | 2024-02-09 | CWW22_2 | Net Zero Carbon Strategy: Reduction of Process Emissions | Implementation of new controls for wastewater treatment processes to reduce emissions of methane and nitrous oxide | Selected | £m | 3 | 6.639 | -0.265 | 6.374 | 7.99 | -0.605 | 7.385 | 7.986 | -0.614 | 7.372 | 8.148 | -0.649 | 7.499 | 7.792 | -0.556 | 7.236 | 38.555 | -2.689 | 35.866 | 100 | 0 | -10045 | -13831.5 | -16453 | -18157 | -19372 | -16244
WSX | WSX PR24-BP-tables-V7-05.02.24.xlsb (sharepoint.com) | 2024-02-05 | CWW22_1 | Heat recovery | Heat recovery (Avo SBR effluent) - displacing fossil gas | Selected | £m | 3 | 1.079 | 0 | 1.079 | 0 | -1.183 | -1.183 | 0 | -1.189 | -1.189 | 0 | -1.195 | -1.195 | 0 | -1.201 | -1.201 | 1.079 | -4.769 | -3.69 |  |  |  | -729.8 | -729.8 | -729.8 | -729.8 | -660.8
WSX | WSX PR24-BP-tables-V7-05.02.24.xlsb (sharepoint.com) | 2024-02-05 | CWW22_2 | Nitrous oxide - standard enhancement | Monitoring & control, 7 sites (out of 20), standard enhancement drivers | Selected | £m | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.506 | 0.108 | 0.614 | 0 | 0.119 | 0.119 | 0 | 0.119 | 0.119 | 0.506 | 0.346 | 0.852 |  |  |  |  | -652.74 | -1305.5 | -1978 | -1976.871
WSX | WSX PR24-BP-tables-V7-05.02.24.xlsb (sharepoint.com) | 2024-02-05 | CWW22_3 | Nitrous oxide - NZ challenge | Monitoring & control, 13 sites (out of 20), net zero carbon challenge | Selected | £m | 3 | 0.627 | 0.117 | 0.744 | 0 | 0.118 | 0.118 | 0.204 | 0.094 | 0.298 | 0 | 0.105 | 0.105 | 0 | 0.105 | 0.105 | 0.831 | 0.538 | 1.37 |  |  |  |  | -294.492 | -589 | -892.4 | -890.529
WSX | WSX PR24-BP-tables-V7-05.02.24.xlsb (sharepoint.com) | 2024-02-05 | CWW22_4 | Transport | Decarbonised Fleet Infrastructure | Selected | £m | 3 | 0.92 | 0.001 | 0.921 | 1.48 | 0.001 | 1.481 | 1.859 | 0.007 | 1.866 | 1.868 | 0.011 | 1.879 | 0.964 | 0.018 | 0.983 | 7.092 | 0.038 | 7.131 | [7 empty] | 3882.9
WSX | WSX PR24-BP-tables-V7-05.02.24.xlsb (sharepoint.com) | 2024-02-05 | CWW22_5 | On-site renewables | 1x 3MW wind turbine on WW land | Feasible | £m | 3 | 3: 0; 6: 0; 9: 0; 12: 0; 13: 3.9; 15: 3.9; 16: 3.9; 17: 0; 18: 3.9 |  |  | -1752 | -3504 | -5256
WSX | WSX PR24-BP-tables-V7-05.02.24.xlsb (sharepoint.com) | 2024-02-05 | CWW22_6 | Exported heat | Heat recovery - large pumping station | Feasible | £m | 3 | 3: 0; 6: 0; 9: 0; 10: 2.5; 11: -0.073; 12: 2.427; 14: -0.146; 15: -0.146; 16: 2.5; 17: -0.219; 18: 2.281 |  |  | -1213.35 | -2426.7 | -3640.05
YKY | YKYSub3_PR24 Data Tables Resubmission 3- 25_01_24_Amended.xlsb (sharepoint.com) | 2024-01-25 | CWW22-1 | Solar | Combination of rooftop and groundmount solar on YW sites. | Selected | £m | 3 | 3.883 | 0 | 3.883 | 4.777 | -0.42 | 4.357 | 4.308 | -1.277 | 3.031 | 2.431 | -2.134 | 0.297 | 1.658 | -2.429 | -0.771 | 17.056 | -6.26 | 10.796 | 100 | 0 | 0 | -1000 | -2000 | -3000 | -3500 | -3000
YKY | YKYSub3_PR24 Data Tables Resubmission 3- 25_01_24_Amended.xlsb (sharepoint.com) | 2024-01-25 | CWW22-2 | Methane reduction | Investment to reduce methane emissions from process via digester upgrade, vacuum degassing and leak detection | Selected | £m | 3 | 8.384 | 0 | 8.384 | 8.611 | 0.037 | 8.648 | 1.452 | -0.248 | 1.204 | 0 | 0.572 | 0.572 | 0 | 0.572 | 0.572 | 18.447 | 0.933 | 19.38 | 0 | 100 | 0 | -6000 | -14000 | -17000 | -18322 | -18182.55
YKY | YKYSub3_PR24 Data Tables Resubmission 3- 25_01_24_Amended.xlsb (sharepoint.com) | 2024-01-25 | CWW22-3 | Nitrous oxide reduction | Investment to reduce nitrous oxide emissions from ASP lanes via use of real time control coupled with monitoring of emission and limited additional investment in liquor buffering. | Selected | £m | 3 | 5.423 | 0 | 5.423 | 3.115 | 0.577 | 3.692 | 0 | 1.153 | 1.153 | 0 | 1.153 | 1.153 | 0 | 1.153 | 1.153 | 8.538 | 4.036 | 12.574 | 100 | 0 | 0 | -2500 | -4500 | -5418 | -5418 | -5371.05
Key input data is the cost and benefits of schemes submitted in business plan table CWW22. The data on this sheet is from companies' orginal submissions from autumn/winter 2023.

## Consolidated Data
#VALUE!
|  | Company | Scheme ID | Scheme name | Selected or Feasible | Totex 2025-26 | Totex 2026-27 | Totex 2027-28 | Totex 2028-29 | Totex 2029-30 | AMP8 totex (£m, 2025-30) | Carbon benefits (cumulated) 2025-26 | Carbon benefits (cumulated) 2026-27 | Carbon benefits (cumulated) 2027-28 | Carbon benefits (cumulated) 2028-29 | Carbon benefits (cumulated) 2029-30 | Scheme benefits (tCO2e cumulative, 2029-30)
| 1 | ANH | CWW22.1 | Cotton Valley STC - Centrate quality | Selected | 0 | 0.481 | 3.432 | 6.035 | 4.619 | 14.567 | 0 | 0 | 0 | 0 | -191.592 | -191.592
| 2 | ANH | CWW22.2 | Cotton Valley STC gas to grid | Selected | 2.254 | 5.521 | 0.511 | 0.511 | 0.511 | 9.309 | 0 | -854.65 | -2563.96 | -4273.25 | -5982.55 | -5982.55
| 3 | ANH | CWW22.3 | Great Billing STC gas to grid | Selected | 1.621 | 4.019 | 0.461 | 0.461 | 0.461 | 7.023 | 0 | -3298.64 | -9895.91 | -16493.18 | -23090.45 | -23090.45
| 4 | ANH | CWW22.4 | Cotton Valley STC Fugitive emissions CH4 | Selected | 0.508 | 3.05 | 1.522 | -0.006 | -0.006 | 5.069 | 0 | 0 | -787.637 | -2362.91 | -3988.18 | -3988.18
| 5 | ANH | CWW22.5 | Whitlingham STC Gas to Grid (AMP8) | Selected | 2.83 | 6.813 | 0.409 | 0.409 | 0.409 | 10.869 | 0 | -1201.18 | -3603.54 | -6005.9 | -8408.26 | -8408.26
| 6 | ANH | CWW22.6 | Great Billing STC Fugitive emissions CH4 | Selected | 0.366 | 2.194 | 0.949 | -0.297 | -0.297 | 2.915 | 0 | 0 | -1222.7 | -3668.09 | -6113.48 | -6113.48
| 7 | ANH | CWW22.7 | Whitlingham STC Fugitive emissions CH4 | Selected | 0.243 | 1.455 | 0.658 | -0.139 | -0.139 | 2.078 | 0 | 0 | -833.831 | -2501.49 | -4169.15 | -4169.15
| 8 | ANH | CWW22.8 | Cliff Quay STC Fugitive Emissions CH4 | Selected | 0.405 | 2.429 | 1.181 | -0.067 | -0.067 | 3.88 | 0 | 0 | -504.698 | -1514.1 | -2523.49 | -2523.49
| 9 | ANH | CWW22.9 | Pyewipe STC Fugitive emissions CH4 | Selected | 0.406 | 2.438 | 1.169 | -0.1 | -0.1 | 3.813 | 0 | 0 | -609.5 | -1828.5 | -3047.5 | -3047.5
| 10 | ANH | CWW22.10 | Colchester STC Fugitive emissions CH4 | Selected | 0.369 | 2.213 | 1.073 | -0.066 | -0.066 | 3.523 | 0 | 0 | -506.359 | -1519.08 | -2531.79 | -2531.79
| 11 | ANH | CWW22.11 | Basildon STC Fugitive emissions CH4 | Selected | 0.41 | 2.461 | 1.22 | -0.022 | -0.022 | 4.047 | 0 | 0 | -17.787 | -56.36 | -88.933 | -88.933
| 12 | ANH | CWW22.12 | Kings Lynn STC Fugitive emissions CH4 | Selected | 0.41 | 2.459 | 1.186 | -0.087 | -0.087 | 3.881 | 0 | 0 | -633.196 | -1899.59 | -3165.98 | -3165.98
| 13 | ANH | CWW22.13 | Cotton Valley WRC Fugitive emissions CH4 | Selected | 0.015 | 0.092 | 0.046 | 0 | 0 | 0.154 | 0 | 0 | -24.36 | -73.08 | -121.8 | -121.8
| 14 | ANH | CWW22.14 | Basildon STC Fugitive emissions N2O | Selected | 0 | 0 | 0.305 | 0.715 | 0.542 | 1.562 | 0 | 0 | 0 | 0 | -174 | -174
| 15 | ANH | CWW22.15 | Colchester STC Fugitive emissions N2O | Selected | 0.287 | 0.573 | 0.587 | 0.027 | 0.027 | 1.5 | 0 | 0 | -116 | -348 | -580 | -580
| 16 | ANH | CWW22.16 | Cliff Quay STC Fugitive emissions N2O | Selected | 0 | 0 | 0.318 | 0.637 | 0.651 | 1.606 | 0 | 0 | 0 | 0 | -273 | -273
| 17 | ANH | CWW22.17 | Whitlingham STC Fugitive Emissions N2O | Selected | 0 | 0 | 0.138 | 0.277 | 0.289 | 0.704 | 0 | 0 | 0 | 0 | -215 | -215
| 18 | ANH | CWW22.18 | Cotton Valley WRC Fugitive emissions N2O | Selected | 0.499 | 1.407 | 2.319 | 1.504 | 0.141 | 5.871 | 0 | 0 | -24.648 | -357.396 | -973.596 | -973.596
| 19 | ANH | CWW22.19 | Great Billing WRC Fugitive Emissions N2O | Selected | 0 | 0.827 | 2.343 | 4.264 | 3.112 | 10.546 | 0 | 0 | 0 | 0 | -540.5 | -540.5
| 20 | ANH | CWW22.20 | Basildon WRC Fugitive Emissions N2O | Selected | 0 | 0.157 | 0.659 | 1.147 | 0.814 | 2.778 | 0 | 0 | 0 | 0 | -341.4 | -341.4
| 21 | ANH | CWW22.21 | Bedford WRC Fugitive Emissions N2O | Selected | 0 | 0.028 | 0.281 | 0.48 | 0.343 | 1.133 | 0 | 0 | 0 | 0 | -365.8 | -365.8
| 22 | ANH | CWW22.22 | Kings Lynn WRC Fugitive Emissions N2O | Selected | 0.19 | 0.381 | 0.381 | 0 | 0 | 0.952 | 0 | 0 | 0 | 0 | -88.6 | -88.6
| 23 | ANH | CWW22.23 | Newton Marsh WRC Fugitive Emissions N2O | Selected | 0 | 0 | 0.089 | 0.179 | 0.179 | 0.447 | 0 | 0 | 0 | 0 | -72.5 | -72.5
| 24 | ANH | CWW22.24 | Broadholme WRC Fugitive Emissions N2O | Selected | 0 | 0 | 0.145 | 0.291 | 0.291 | 0.727 | 0 | 0 | 0 | 0 | -181.1 | -181.1
| 25 | ANH | CWW22.25 | Letchworth WRC Fugitive emissions N2O | Selected | 0 | 0.889 | 2.519 | 4.586 | 3.36 | 11.355 | 0 | 0 | 0 | 0 | -127.6 | -127.6
| 26 | ANH | CWW22.26 | Newmarket WRC Fugitive Emissions N2O | Selected | 0 | 0 | 0.919 | 1.839 | 1.85 | 4.608 | 0 | 0 | 0 | 0 | -26.5 | -26.5
| 27 | ANH | CWW22.27 | Hitchin WRC Fugitive emissions N2O | Selected | 0 | 0.046 | 0.326 | 0.56 | 0.47 | 1.402 | 0 | 0 | 0 | 0 | -32.95 | -32.95
| 28 | ANH | CWW22.28 | Dunstable WRC Fugitive Emissions N2O | Selected | 0 | 0.96 | 2.72 | 4.951 | 3.67 | 12.301 | 0 | 0 | 0 | 0 | -75.3 | -75.3
| 29 | ANH | CWW22.29 | Flitwick WRC Fugitive Emissions N2O | Selected | 0.527 | 1.468 | 2.573 | 1.769 | 0.116 | 6.453 | 0 | 0 | -3.532 | -51.214 | -139.514 | -139.514
| 30 | ANH | CWW22.30 | Great Billing STC Liquor Ammonia | Selected | 0 | 0.239 | 1.705 | 2.924 | 2.511 | 7.379 | 0 | 0 | 0 | 0 | -557 | -557
| 31 | ANH | CWW22.31 | Logistics Fleet CO2 emissions 2025-26 | Selected | 1.114 | -0.239 | -0.239 | -0.239 | -0.239 | 0.159 | -770.646 | -1514.292 | -2311.938 | -3082.584 | -3853.23 | -3853.23
| 32 | ANH | CWW22.32 | Logistics fleet CO2 emissions 2026-27 | Selected | 0 | 1.433 | -0.187 | -0.187 | -0.187 | 0.873 | 0 | -577.988 | -1155.976 | -1733.964 | -2311.952 | -2311.952
| 33 | ANH | CWW22.33 | Logistics fleet CO2 emissions 2027-28 | Selected | 0 | 0 | 1.805 | -0.249 | -0.249 | 1.307 | 0 | 0 | -770.616 | -1514.292 | -2311.938 | -2311.938
| 34 | ANH | CWW22.34 | Logistics fleet CO2 emissions 2028-29 | Selected | 0 | 0 | 0 | 1.573 | -0.217 | 1.356 | 0 | 0 | 0 | -674.286 | -1348.572 | -1348.572
| 35 | ANH | CWW22.35 | Logistics fleet CO2 emissions 2029-30 | Selected | 0 | 0 | 0 | 0 | 3.922 | 3.922 | 0 | 0 | 0 | 0 | -1830.29 | -1830.29
| 36 | ANH | CWW22.36 | Huntingdon WRC Fugitive Emissions N2O | Selected | 0 | 0 | 0 | 0.91 | 1.881 | 2.791 | 0 | 0 | 0 | 0 | -87.3 | -87.3
| 37 | ANH | CWW22.37 | AMP8 Small Scale Solar Delivery WR | Feasible | 2.017 | 1.777 | 1.536 | 1.296 | 1.055 | 7.681 | 0 | -454.48 | -1363.74 | -2727.48 | -4545.8 | -4545.8
| 38 | ANH | CWW22.38 | Basildon STC Gas to Grid | Feasible | 1.5 | 3.376 | 3.352 | 2.437 | 2.101 | 12.766 | 0 | 0 | 0 | -1088.74 | -2177.48 | -2177.48
| 39 | ANH | CWW22.39 | Colchester STC Gas to Grid | Feasible | 1.5 | 3.376 | 3.352 | 3.147 | 2.953 | 14.328 | 0 | 0 | 0 | -1324.84 | -2649.68 | -2649.68
| 40 | ANH | CWW22.40 | Ipswich Cliff Quay STC Gas to Grid | Feasible | 1.5 | 3.376 | 3.352 | 3.038 | 2.822 | 14.088 | 0 | 0 | 0 | -1692.08 | -3384.16 | -3384.16
| 41 | ANH | CWW22.41 | Pyewipe STC Gas to Grid | Feasible | 1.5 | 3.376 | 3.352 | 3.073 | 2.864 | 14.165 | 0 | 0 | 0 | -3361 | -6722 | -6722
| 42 | ANH | CWW22.42 | Kings Lynn STC gas to grid | Feasible | 1.5 | 3.376 | 3.352 | 3.303 | 3.141 | 14.672 | 0 | 0 | 0 | -3360 | -6720 | -6720
| 43 | ANH | CWW22.43 | Whitlingham WRC Fugitive Emissions N2O | Feasible | 0 | 0 | 0 | 0.967 | 0 | 0.967 | 0 | 0 | 0 | 0 | -418.8 | -418.8
| 44 | ANH | CWW22.44 | Colchester WRC Fugitive Emissions N2O | Feasible | 0 | 0 | 0.831 | 0.831 | 0 | 1.662 | 0 | 0 | 0 | 0 | -192.5 | -192.5
| 45 | ANH | CWW22.45 | Colchester WRC Fugitive Emissions N2O | Feasible | 3.121 | 7.282 | 0.021 | 0.021 | 0.021 | 10.466 | 0 | 0 | -264.7 | -529.4 | -794.1 | -794.1
| 46 | HDD | CWW22.1 | Process Emissions Reduction | Selected | 0.491 | 0.296 | 0.025 | 0.025 | 0.025 | 0.864 | 0 | 0 | -137.13 | -274.265 | -411.398 | -411.398
| 47 | HDD | CWW22.2 | Heat Decarbonisation | Selected | 0.038 | 0 | 0 | 0 | 0 | 0.038 | 0 | -5.473 | -10.947 | -16.42 | -21.893 | -21.893
| 48 | SVE | NZ#1 | Digital Twin | Selected | 12.786 | 25.571 | -2.118 | 8.551 | 8.551 | 53.341 | 0 | 0 | -5939.59 | -17818.77 | -35637.54 | -35637.54
| 49 | SVE | NZ#2 | Cover & Treat | Selected | 18.579 | 18.579 | 18.579 | 18.579 | 18.579 | 92.895 | 0 | 0 | -7607.71 | -23251.86 | -74239.11 | -74239.11
| 50 | SVE | NZ#3 | ASP Intensification | Selected | 4.076 | 28.561 | 25.891 | 23.954 | 21.629 | 104.111 | 0 | 0 | -8326.56 | -24979.68 | -49959.36 | -49959.36
| 51 | SVE | NZ#4 | Active gas capture | Selected | 0 | 0 | 33.179 | 22.33 | 35.77 | 91.279 | 0 | 0 | -8013.61 | -24040.83 | -48081.66 | -48081.66
| 52 | SVE | NZ#5 | EV Charging Infrastructure | Selected | 0 | 0.72 | 0 | 0 | 0 | 0.72 | 0 | 0 | -311.4 | -934.2 | -1868.4 | -1868.4
| 53 | SVE | NZ#6 | Heat pumps | Selected | 6.598 | 0 | -0.06 | -0.09 | -0.09 | 6.358 | 0 | 0 | -209.25 | -627.75 | -1255.5 | -1255.5
| 54 | SVE | NZ#7 | HVO diesel replacement | Selected | 0.271 | 0 | 0 | 0 | 0 | 0.271 | 0 | 0 | -567 | -1701 | -3402 | -3402
| 55 | SVE | NZ#8 | Cellulose recovery | Selected | 0 | 0 | 31.772 | 31.772 | -0.469 | 63.075 | 0 | 0 | -1516.8 | -7810.4 | -15620.8 | -15620.8
| 56 | SVE | NZ#9 | Process Optimisation | Selected | 6.045 | 0 | 0.738 | 1.092 | 1.092 | 8.967 | 0 | 0 | -34000 | -68000 | -102000 | -102000
| 57 | SVE | NZ#10 | Hydrogen Production | Feasible | 0.45 | 0.45 | 0.237 | 0.237 | 0.237 | 1.611 | 0 | 0 | -806.4 | -1612.8 | -2419.2 | -2419.2
| 58 | SVE | NZ#11 | Electrical storage | Feasible | 0.99 | 0.99 | 0.577 | 0.577 | 0.577 | 3.711 | 0 | 0 | -32.85 | -65.7 | -98.55 | -98.55
| 59 | SVE | NZ#12 | EV fleet only | Feasible | 0.657 | 0.657 | 0.657 | 0.657 | 0.657 | 3.285 | 0 | 0 | -1557 | -3114 | -4671 | -4671
| 60 | SVE | NZ#13 | HVO fuel only | Feasible | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 1.8 | -2271.6 | -4543.2 | -6814.8 | -9086.4 | -11358 | -11358
| 61 | SVE | NZ#14 | Solar PV | Feasible | 2.34 | 2.34 | -0.285 | -0.285 | -0.285 | 3.825 | 0 | 0 | -2625.37 | -5250.74 | -7876.12 | -7876.12
| 62 | TMS | CWW22_1 | S40749/1 (Long Reach - Installation of Biomethane Plant - Delta from botex for bidding process) | Feasible | 5.886 | 3.747 | 2.985 | 3.018 | 3.186 | 18.822 | 0 | 0 | -2537.57 | -5075.14 | -7612.71 | -7612.71
| 63 | TMS | CWW22_2 | Aylesbury - Installation of Biomethane Plant with heat pump - Delta from botex for bidding process | Feasible | 0 | 1.107 | 0.371 | 0.472 | 0.5 | 2.45 | 0 | 0 | 0 | -476.348 | -952.697 | -952.697
| 64 | TMS | CWW22_3 | Bishop Stortford - Installation of Biomethane Plant - enhancement from botex for bidding process | Feasible | 0 | 0 | 0 | 0.355 | 0.258 | 0.613 | 0 | 0 | 0 | -290.137 | -581.009 | -581.009
| 65 | TMS | CWW22_4 | Didcot - Installation of Biomethane Plant - enhancement from botex for bidding process | Feasible | 0 | 0.1 | 0.112 | 0.115 | 0.126 | 0.453 | 0 | -369.425 | -677.409 | -985.392 | -1293.376 | -1293.376
| 66 | TMS | CWW22_5 | East Hyde - Installation of Biomethane Plant - enhancement from botex for bidding process | Feasible | 0 | 0 | 0 | 0.519 | 0.555 | 1.074 | 0 | 0 | 0 | -558.252 | -1116.504 | -1116.504
| 67 | TMS | CWW22_6 | Hogsmill -Installation of Biomethane Plant - enhancement from botex for bidding process | Feasible | 0 | 1.777 | 1.185 | 1.239 | 1.303 | 5.504 | 0 | 0 | 0 | -1109.173 | -2219.814 | -2219.814
| 68 | TMS | CWW22_7 | Reading - Installation of Biomethane Plant - enhancement from botex for bidding process | Feasible | 0 | 0 | 0 | 0.923 | 1.044 | 1.967 | 0 | 0 | 0 | -1040.033 | -2138.606 | -2138.606
| 69 | TMS | CWW22_8 | S40040/4 (PR24 Fleet - Life expired Enhancement (cost to convert to electrical) (Waste)) | Feasible | 6.717 | 6.028 | 4.727 | 3.199 | 0.139 | 20.81 | -1212 | -3150 | -5770 | -9140 | -13142 | -13142
| 70 | TMS | CWW22_9 | S40841/1 (PR24 Hybrid air source heat pump/existing boiler for 4 corporate offices (Waste)) | Feasible | 0.605 | 0.529 | -0.054 | -0.037 | -0.025 | 1.018 | -198.77 | -596.3 | -993.83 | -1391.36 | -1788.89 | -1788.89
| 71 | TMS | CWW22_10 | S40842/2 (PR24 Air source heat pump for site office (enhancement cost) (Waste)) | Feasible | 0.506 | 0.525 | 0.546 | 0.567 | 0.591 | 2.735 | -50 | -150.019 | -300.038 | -500.067 | -750.066 | -750.066
| 72 | NWT | E00001337 | Stationary fossil fuel reductions | Selected | 9.073 | 1.453 | 0.439 | 0.977 | 0.819 | 12.761 | -7055.38 | -14110.76 | -21166.14 | -28221.52 | -35276.9 | -35276.9
| 73 | NWT | E00001338 | Process emissions (Bioresources) | Selected | 7.293 | 7.409 | -0.287 | -0.325 | -0.314 | 13.776 | 0 | 0 | -7358.919 | -14717.838 | -22076.757 | -22076.757
| 74 | NWT | E00001339 | Process emissions (Wastewater) | Selected | 27.22 | 1.698 | 1.713 | 1.712 | 1.76 | 34.104 | 0 | 0 | -12541.041 | -37623.123 | -62705.206 | -62705.206
| 75 | NWT | E00001340 | Transport fossil fuel reductions - Green fleet LCVs phase 1 | Selected | 1.543 | 1.603 | 3.068 | 1.811 | -2.217 | 5.808 | -337.89 | -1436.031 | -3801.258 | -7727.535 | -12370.138 | -12370.138
| 76 | NWT | E00001341 | Transport fossil fuel reductions - Green fleet LCVs phase 2 | Selected | 1.928 | 2.327 | 4.58 | 3.656 | -0.766 | 11.725 | -116.822 | -496.493 | -1314.245 | -2671.714 | -4276.845 | -4276.845
| 77 | NWT | E00001342 | Transport fossil fuel reductions - Green fleet Biomethane HGVs | Selected | 0.294 | 0.272 | 0.244 | 0.221 | 0.193 | 1.224 | -154.634 | -618.538 | -1391.71 | -2474.152 | -3865.862 | -3865.862
| 78 | NWT | E00001426 | Phase 2 – Further low regrets emissions reductions in AMP8 | Selected | 0 | 0 | 20.051 | 20.357 | 20.293 | 60.701 | 0 | 0 | -13229.009 | -26458.018 | -39687.026 | -39687.026
| 79 | NWT | E00001346 | Property emissions reductions | Selected | 2.411 | 0 | 0 | 0 | 0 | 2.411 | -816.324 | -1632.648 | -2448.972 | -3265.296 | -4081.62 | -4081.62
| 80 | NWT | E00001425 | Net zero catchment strategy | Selected | 0.504 | 0.256 | 0.153 | 0.103 | 0 | 1.016 | 0 | 0 | 0 | 0 | 0 | 0
| 81 | WSH | CWW22_1 | Net Zero Carbon Strategy: Network Control Systems (Wastewater) | Selected | 0.132 | 0.297 | 0.297 | 0.313 | 0.265 | 1.304 | -50 | -165 | -285 | -400 | -500 | -500
| 82 | WSH | CWW22_2 | Net Zero Carbon Strategy: Reduction of Process Emissions | Selected | 6.374 | 7.385 | 7.372 | 7.499 | 7.236 | 35.866 | -10045 | -13831.5 | -16453 | -18157 | -19372 | -19372
| 83 | WSX | CWW22_1 | Heat recovery | Selected | 1.079 | -1.183 | -1.189 | -1.195 | -1.201 | -3.69 | 0 | -729.8 | -729.8 | -729.8 | -729.8 | -729.8
| 84 | WSX | CWW22_2 | Nitrous oxide - standard enhancement | Selected | 0 | 0 | 0.614 | 0.119 | 0.119 | 0.852 | 0 | 0 | -652.74 | -1305.5 | -1978 | -1978
| 85 | WSX | CWW22_3 | Nitrous oxide - NZ challenge | Selected | 0.744 | 0.118 | 0.298 | 0.105 | 0.105 | 1.37 | 0 | 0 | -294.492 | -589 | -892.4 | -892.4
| 86 | WSX | CWW22_4 | Transport | Selected | 0.921 | 1.481 | 1.866 | 1.879 | 0.983 | 7.131 | 0 | 0 | 0 | 0 | 0 | 0
| 87 | WSX | CWW22_5 | On-site renewables | Feasible | 0 | 0 | 0 | 0 | 3.9 | 3.9 | 0 | 0 | -1752 | -3504 | -5256 | -5256
| 88 | WSX | CWW22_6 | Exported heat | Feasible | 0 | 0 | 0 | 2.427 | -0.146 | 2.281 | 0 | 0 | -1213.35 | -2426.7 | -3640.05 | -3640.05
| 89 | YKY | CWW22-1 | Solar | Selected | 3.883 | 4.357 | 3.031 | 0.297 | -0.771 | 10.796 | 0 | -1000 | -2000 | -3000 | -3500 | -3500
| 90 | YKY | CWW22-2 | Methane reduction | Selected | 8.384 | 8.648 | 1.204 | 0.572 | 0.572 | 19.38 | 0 | -6000 | -14000 | -17000 | -18322 | -18322
| 91 | YKY | CWW22-3 | Nitrous oxide reduction | Selected | 5.423 | 3.692 | 1.153 | 1.153 | 1.153 | 12.574 | 0 | -2500 | -4500 | -5418 | -5418 | -5418
| 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Input Override
#VALUE!
DD BPT link | Scheme resubmitted at DD |  | Company | Scheme ID | Scheme name | Selected or Feasible | Totex 2025-26 | Totex 2026-27 | Totex 2027-28 | Totex 2028-29 | Totex 2029-30 | AMP8 totex (£m, 2025-30) | Carbon benefits (cumulated) 2025-26 | Carbon benefits (cumulated) 2026-27 | Carbon benefits (cumulated) 2027-28 | Carbon benefits (cumulated) 2028-29 | Carbon benefits (cumulated) 2029-30 | Scheme benefits (tCO2e cumulative, 2029-30) | Reason for override | Reason for override 2
ANH_DD_004-v7-Main-data-tables.xlsb | Yes | 1 | ANH | CWW22.1 | Cotton Valley STC - Centrate quality | Selected | 0 | 0.48865 | 3.4843 | 6.126 | 4.5286 | 14.6275 |  |  |  |  | -287.5 | -287.5 | Approved at DD and included in company representation response to DD.
ANH_DD_004-v7-Main-data-tables.xlsb | No | 2 | ANH | CWW22.2 | Cotton Valley STC gas to grid | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rejected at DD: no company representation.
ANH_DD_004-v7-Main-data-tables.xlsb | No | 3 | ANH | CWW22.3 | Great Billing STC gas to grid | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rejected at DD: no company representation.
ANH_DD_004-v7-Main-data-tables.xlsb | No | 4 | ANH | CWW22.4 | Cotton Valley STC Fugitive emissions CH4 | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rejected at DD: no company representation.
ANH_DD_004-v7-Main-data-tables.xlsb | No | 5 | ANH | CWW22.5 | Whitlingham STC Gas to Grid (AMP8) | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rejected at DD: no company representation.
ANH_DD_004-v7-Main-data-tables.xlsb | No | 6 | ANH | CWW22.6 | Great Billing STC Fugitive emissions CH4 | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rejected at DD: no company representation.
ANH_DD_004-v7-Main-data-tables.xlsb | No | 7 | ANH | CWW22.7 | Whitlingham STC Fugitive emissions CH4 | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rejected at DD: no company representation.
ANH_DD_004-v7-Main-data-tables.xlsb | No | 8 | ANH | CWW22.8 | Cliff Quay STC Fugitive Emissions CH4 | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rejected at DD: no company representation.
ANH_DD_004-v7-Main-data-tables.xlsb | No | 9 | ANH | CWW22.9 | Pyewipe STC Fugitive emissions CH4 | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rejected at DD: no company representation.
ANH_DD_004-v7-Main-data-tables.xlsb | No | 10 | ANH | CWW22.10 | Colchester STC Fugitive emissions CH4 | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rejected at DD: no company representation.
ANH_DD_004-v7-Main-data-tables.xlsb | No | 11 | ANH | CWW22.11 | Basildon STC Fugitive emissions CH4 | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rejected at DD: no company representation.
ANH_DD_004-v7-Main-data-tables.xlsb | No | 12 | ANH | CWW22.12 | Kings Lynn STC Fugitive emissions CH4 | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rejected at DD: no company representation.
ANH_DD_004-v7-Main-data-tables.xlsb | No | 13 | ANH | CWW22.13 | Cotton Valley WRC Fugitive emissions CH4 | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rejected at DD: no company representation.
ANH_DD_004-v7-Main-data-tables.xlsb | Yes | 14 | ANH | CWW22.14 | Basildon STC Fugitive emissions N2O | Selected | 0 | 0 | 0.30472 | 0.71523 | 0.53552 | 1.5555 |  |  |  |  | -174 | -174 | Approved at DD and included in company representation response to DD.
ANH_DD_004-v7-Main-data-tables.xlsb | Yes | 15 | ANH | CWW22.15 | Colchester STC Fugitive emissions N2O | Selected | 0.28658 | 0.57316 | 0.5807 | 0.010084 | 0.020609 | 1.4711 |  |  | -116 | -348 | -580 | -580 | Approved at DD and included in company representation response to DD.
ANH_DD_004-v7-Main-data-tables.xlsb | Yes | 16 | ANH | CWW22.16 | Cliff Quay STC Fugitive emissions N2O | Selected | 0 | 0 | 0.31847 | 0.63695 | 0.64461 | 1.6 |  |  |  |  | -273 | -273 | Approved at DD and included in company representation response to DD.
ANH_DD_004-v7-Main-data-tables.xlsb | Yes | 17 | ANH | CWW22.17 | Whitlingham STC Fugitive Emissions N2O | Selected | 0 | 0 | 0.13846 | 0.27691 | 0.28579 | 0.70116 |  |  |  |  | -215 | -215 | Rejected at DD: company representation.
ANH_DD_004-v7-Main-data-tables.xlsb | Yes | 18 | ANH | CWW22.18 | Cotton Valley WRC Fugitive emissions N2O | Selected | 0.34027 | 0.68053 | 0.68053 | 0 | 0 | 1.7013 |  |  | -35.417 | -460.417 | -885.417 | -885.417 | Rejected at DD: company representation.
ANH_DD_004-v7-Main-data-tables.xlsb | Yes | 19 | ANH | CWW22.19 | Great Billing WRC Fugitive Emissions N2O | Selected | 0 | 0.41339 | 0.82677 | 0.82692 | 0.000274 | 2.0673 |  |  |  | -34.65 | -450.45 | -450.45 | Rejected at DD: company representation.
ANH_DD_004-v7-Main-data-tables.xlsb | Yes | 20 | ANH | CWW22.20 | Basildon WRC Fugitive Emissions N2O | Selected | 0 | 0.12178 | 0.49044 | 0.74134 | 0.40749 | 1.7611 |  |  |  | -42.85 | -214.25 | -214.25 | Rejected at DD: company representation.
ANH_DD_004-v7-Main-data-tables.xlsb | Yes | 21 | ANH | CWW22.21 | Bedford WRC Fugitive Emissions N2O | Selected | 0 | 0.03742 | 0.1871 | 0.29938 | 0.22459 | 0.74849 |  |  |  | -63.05 | -315.25 | -315.25 | Rejected at DD: company representation.
ANH_DD_004-v7-Main-data-tables.xlsb | Yes | 22 | ANH | CWW22.22 | Kings Lynn WRC Fugitive Emissions N2O | Selected | 0.19039 | 0.38078 | 0.38078 | 0 | 0 | 0.95194 |  |  | -44.3 | -132.9 | -221.5 | -221.5 | Rejected at DD: company representation.
ANH_DD_004-v7-Main-data-tables.xlsb | Yes | 23 | ANH | CWW22.23 | Newton Marsh WRC Fugitive Emissions N2O | Selected | 0 | 0 | 0.089361 | 0.17872 | 0.17872 | 0.4468 |  |  |  |  | -72.5 | -72.5 | Rejected at DD: company representation.
ANH_DD_004-v7-Main-data-tables.xlsb | Yes | 24 | ANH | CWW22.24 | Broadholme WRC Fugitive Emissions N2O | Selected | 0.16084 | 0.28268 | 0.20442 | 0 | 0 | 0.64794 |  |  | -10.408 | -135.308 | -260.208 | -260.208 | Rejected at DD: company representation.
ANH_DD_004-v7-Main-data-tables.xlsb | Yes | 25 | ANH | CWW22.25 | Letchworth WRC Fugitive emissions N2O | Selected | 0 | 0.88886 | 2.5194 | 4.586 | 3.3527 | 11.3471 |  |  |  |  | -127.6 |  | Approved at DD and included in company representation response to DD.
ANH_DD_004-v7-Main-data-tables.xlsb | Yes | 26 | ANH | CWW22.26 | Newmarket WRC Fugitive Emissions N2O | Selected | 0 | 0 | 0.91948 | 1.839 | 1.8498 | 4.6082 |  |  |  |  | -26.5 |  | Approved at DD and included in company representation response to DD.
ANH_DD_004-v7-Main-data-tables.xlsb | Yes | 27 | ANH | CWW22.27 | Hitchin WRC Fugitive emissions N2O | Selected | 0 | 0.052293 | 0.20917 | 0.31376 | 0.20917 | 0.7844 |  |  |  | -12.675 | -63.375 |  | Rejected at DD: company representation.
ANH_DD_004-v7-Main-data-tables.xlsb | Yes | 28 | ANH | CWW22.28 | Dunstable WRC Fugitive Emissions N2O | Selected | 0 | 0.95962 | 2.72 | 4.9511 | 3.6432 | 12.274 |  |  |  |  | -75.3 |  | Approved at DD and included in company representation response to DD.
ANH_DD_004-v7-Main-data-tables.xlsb | Yes | 29 | ANH | CWW22.29 | Flitwick WRC Fugitive Emissions N2O | Selected | 0.52737 | 1.4682 | 2.5719 | 1.7562 | 0.097275 | 6.4209 |  |  | -3.532 | -51.214 | -139.514 |  | Approved at DD and included in company representation response to DD.
ANH_DD_004-v7-Main-data-tables.xlsb | No | 30 | ANH | CWW22.30 | Great Billing STC Liquor Ammonia | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rejected at DD: no company representation.
ANH_DD_004-v7-Main-data-tables.xlsb | No | 31 | ANH | CWW22.31 | Logistics Fleet CO2 emissions 2025-26 | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rejected at DD: no company representation.
ANH_DD_004-v7-Main-data-tables.xlsb | No | 32 | ANH | CWW22.32 | Logistics fleet CO2 emissions 2026-27 | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rejected at DD: no company representation.
ANH_DD_004-v7-Main-data-tables.xlsb | No | 33 | ANH | CWW22.33 | Logistics fleet CO2 emissions 2027-28 | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rejected at DD: no company representation.
ANH_DD_004-v7-Main-data-tables.xlsb | No | 34 | ANH | CWW22.34 | Logistics fleet CO2 emissions 2028-29 | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rejected at DD: no company representation.
ANH_DD_004-v7-Main-data-tables.xlsb | No | 35 | ANH | CWW22.35 | Logistics fleet CO2 emissions 2029-30 | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rejected at DD: no company representation.
ANH_DD_004-v7-Main-data-tables.xlsb | Yes | 36 | ANH | CWW22.36 | Huntingdon WRC Fugitive Emissions N2O | Selected | 0 | 0 | 0 | 0.17376 | 0.35927 | 0.53303 |  |  |  |  | -60.2 | -60.2 | Rejected at DD: company representation.
ANH_DD_004-v7-Main-data-tables.xlsb | No | 37 | ANH | CWW22.37 | AMP8 Small Scale Solar Delivery WR | Feasible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rejected at DD: no company representation.
ANH_DD_004-v7-Main-data-tables.xlsb | No | 38 | ANH | CWW22.38 | Basildon STC Gas to Grid | Feasible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rejected at DD: no company representation.
ANH_DD_004-v7-Main-data-tables.xlsb | No | 39 | ANH | CWW22.39 | Colchester STC Gas to Grid | Feasible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rejected at DD: no company representation.
ANH_DD_004-v7-Main-data-tables.xlsb | No | 40 | ANH | CWW22.40 | Ipswich Cliff Quay STC Gas to Grid | Feasible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rejected at DD: no company representation.
ANH_DD_004-v7-Main-data-tables.xlsb | No | 41 | ANH | CWW22.41 | Pyewipe STC Gas to Grid | Feasible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rejected at DD: no company representation.
ANH_DD_004-v7-Main-data-tables.xlsb | No | 42 | ANH | CWW22.42 | Kings Lynn STC gas to grid | Feasible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rejected at DD: no company representation.
ANH_DD_004-v7-Main-data-tables.xlsb | No | 43 | ANH | CWW22.43 | Whitlingham WRC Fugitive Emissions N2O | Feasible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rejected at DD: no company representation.
ANH_DD_004-v7-Main-data-tables.xlsb | No | 44 | ANH | CWW22.44 | Colchester WRC Fugitive Emissions N2O | Feasible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rejected at DD: no company representation.
ANH_DD_004-v7-Main-data-tables.xlsb | Yes | 45 | ANH | CWW22.45 | Colchester WRC Fugitive Emissions N2O | Feasible | 0.93235 | 2.6427 | 4.8104 | 3.531 | 0.041357 | 11.958 |  |  |  | -22.058 | -286.758 | -286.758 | Approved at DD and included in company representation response to DD.
24.09.19 - HDD Original set BPDTs.xlsx | Yes | 46 | HDD | CWW22.1 | Process Emissions Reduction | Selected | 0.49147 | 0.29561 | 0.025488 | 0.025488 | 0.025488 | 0.86355 |  |  | -137.13 | -274.265 | -411.3975 |  | Approved at DD and included in company representation response to DD.
24.09.19 - HDD Original set BPDTs.xlsx | No | 47 | HDD | CWW22.2 | Heat Decarbonisation | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rejected at DD: no company representation.
24 09 12 - SVE BPDTS.xlsx | Yes | 48 | SVE | NZ#1 | Digital Twin | Selected | 12.786 | 25.571 | -2.118 | 8.551 | 8.551 | 53.341 | 0 | 0 | -1400 | -4300 | -8600 | -8600 | Approved at DD and included in company representation response to DD.
24 09 12 - SVE BPDTS.xlsx | Yes | 49 | SVE | NZ#2 | Cover & Treat | Selected | 18.579 | 18.579 | 18.579 | 18.579 | 18.579 | 92.895 | 0 | 0 | -7607.71 | -23251.86 | -74239.11 | -74239.11 | Approved at DD and included in company representation response to DD.
24 09 12 - SVE BPDTS.xlsx | Yes | 50 | SVE | NZ#3 | ASP Intensification | Selected | 4.076 | 28.561 | 25.891 | 23.954 | 21.629 | 104.111 | 0 | 0 | -8326.56 | -24979.68 | -49959.36 | -49959.36 | Approved at DD and included in company representation response to DD.
24 09 12 - SVE BPDTS.xlsx | Yes | 51 | SVE | NZ#4 | Active gas capture | Selected | 0 | 0 | 12.948 | 8.714 | 13.959 | 35.621 | 0 | 0 | -1359 | -4078 | -8156 | -13593 | Rejected at DD: company representation. | Scheme has been split to remove in-series digestion which is not deemed acceptable. Updated figures reflect the cost and benefits of vacuum degassing only. (Query OFW-REP-SVE-114)
24 09 12 - SVE BPDTS.xlsx | Yes | 52 | SVE | NZ#5 | EV Charging Infrastructure | Selected | 0 | 0.72 | 0 | 0 | 0 | 0.72 | 0 | 0 | -311.4 | -934.2 | -1868.4 | -1868.4 | Rejected at DD: company representation.
24 09 12 - SVE BPDTS.xlsx | Yes | 53 | SVE | NZ#6 | Heat pumps | Selected | 6.598 | 0 | -0.06 | -0.09 | -0.09 | 6.358 | 0 | 0 | -209.25 | -627.75 | -1255.5 | -1255.5 | Rejected at DD: company representation.
24 09 12 - SVE BPDTS.xlsx | Yes | 54 | SVE | NZ#7 | HVO diesel replacement | Selected | 0.271 | 0 | 0 | 0 | 0 | 0.271 | 0 | 0 | -567 | -1701 | -3402 | -3402 | Rejected at DD: company representation.
24 09 12 - SVE BPDTS.xlsx | Yes | 55 | SVE | NZ#8 | Cellulose recovery | Selected | 0 | 0 | 31.772 | 31.772 | -0.469 | 63.075 | 0 | 0 | -1516.8 | -7810.4 | -15620.8 | -15620.8 | Rejected at DD: company representation.
24 09 12 - SVE BPDTS.xlsx | Yes | 56 | SVE | NZ#9 | Process Optimisation | Selected | 6.045 | 0 | 0.738 | 1.092 | 1.092 | 8.967 | 0 | 0 | -8200 | -16400 | -24600 | -24600 | Rejected at DD: company representation.
24 09 12 - SVE BPDTS.xlsx | Yes | 57 | SVE | NZ#10 | Hydrogen Production | Feasible | 0.45 | 0.45 | 0.237 | 0.237 | 0.237 | 1.611 | 0 | 0 | -806.4 | -1612.8 | -2419.2 | -2419.2 | Rejected at DD: company representation.
24 09 12 - SVE BPDTS.xlsx | Yes | 58 | SVE | NZ#11 | Electrical storage | Feasible | 0.99 | 0.99 | 0.577 | 0.577 | 0.577 | 3.711 | 0 | 0 | -32.85 | -65.7 | -98.55 | -98.55 | Rejected at DD: company representation.
24 09 12 - SVE BPDTS.xlsx | Yes | 59 | SVE | NZ#12 | EV fleet only | Feasible | 0.657 | 0.657 | 0.657 | 0.657 | 0.657 | 3.285 | 0 | 0 | -1557 | -3114 | -4671 | -4671 | Rejected at DD: company representation.
24 09 12 - SVE BPDTS.xlsx | Yes | 60 | SVE | NZ#13 | HVO fuel only | Feasible | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 1.8 | -2271.6 | -4543.2 | -6814.8 | -9086.4 | -11358 | -11358 | Rejected at DD: company representation.
24 09 12 - SVE BPDTS.xlsx | Yes | 61 | SVE | NZ#14 | Solar PV | Feasible | 2.34 | 2.34 | -0.285 | -0.285 | -0.285 | 3.825 | 0 | 0 | -2625.37 | -5250.74 | -7876.12 | -7876.12 | Rejected at DD: company representation.
TMS-DD-002-PR24-Draft-Determination-Data-Tables.xlsb | Yes | 62 | TMS | CWW22_1 | S40749/1 (Long Reach - Installation of Biomethane Plant - Delta from botex for bidding process) | Feasible | 5.886 | 3.747 | 2.985 | 3.018 | 3.186 | 18.822 | 0 | 0 | -2537.57 | -5075.14 | -7612.71 | -7612.71 | Rejected at DD: company representation.
TMS-DD-002-PR24-Draft-Determination-Data-Tables.xlsb | Yes | 63 | TMS | CWW22_2 | Aylesbury - Installation of Biomethane Plant with heat pump - Delta from botex for bidding process | Feasible | 0 | 1.107 | 0.371 | 0.472 | 0.5 | 2.45 | 0 | 0 | 0 | -476.348 | -952.697 | -952.697 | Rejected at DD: company representation.
TMS-DD-002-PR24-Draft-Determination-Data-Tables.xlsb | Yes | 64 | TMS | CWW22_3 | Bishop Stortford - Installation of Biomethane Plant - enhancement from botex for bidding process | Feasible | 0 | 0 | 0 | 0.355 | 0.258 | 0.613 | 0 | 0 | 0 | -290.137 | -581.009 | -581.009 | Rejected at DD: company representation.
TMS-DD-002-PR24-Draft-Determination-Data-Tables.xlsb | Yes | 65 | TMS | CWW22_4 | Didcot - Installation of Biomethane Plant - enhancement from botex for bidding process | Feasible | 0 | 0.1 | 0.112 | 0.115 | 0.126 | 0.453 | 0 | -369.425 | -677.409 | -985.392 | -1293.376 | -1293.376 | Rejected at DD: company representation.
TMS-DD-002-PR24-Draft-Determination-Data-Tables.xlsb | Yes | 66 | TMS | CWW22_5 | East Hyde - Installation of Biomethane Plant - enhancement from botex for bidding process | Feasible | 0 | 0 | 0 | 0.519 | 0.555 | 1.074 | 0 | 0 | 0 | -558.252 | -1116.504 | -1116.504 | Rejected at DD: company representation.
TMS-DD-002-PR24-Draft-Determination-Data-Tables.xlsb | Yes | 67 | TMS | CWW22_6 | Hogsmill -Installation of Biomethane Plant - enhancement from botex for bidding process | Feasible | 0 | 1.777 | 1.185 | 1.239 | 1.303 | 5.504 | 0 | 0 | 0 | -1109.173 | -2219.814 | -2219.814 | Rejected at DD: company representation.
TMS-DD-002-PR24-Draft-Determination-Data-Tables.xlsb | Yes | 68 | TMS | CWW22_7 | Reading - Installation of Biomethane Plant - enhancement from botex for bidding process | Feasible | 0 | 0 | 0 | 0.923 | 1.044 | 1.967 | 0 | 0 | 0 | -1040.033 | -2138.606 | -2138.606 | Rejected at DD: company representation.
TMS-DD-002-PR24-Draft-Determination-Data-Tables.xlsb | Yes | 69 | TMS | CWW22_8 | S40040/4 (PR24 Fleet - Life expired Enhancement (cost to convert to electrical) (Waste)) | Feasible | 6.717 | 6.028 | 4.727 | 3.199 | 0.139 | 20.81 | -1212 | -3150 | -5770 | -9140 | -13142 | -13142 | Rejected at DD: company representation.
TMS-DD-002-PR24-Draft-Determination-Data-Tables.xlsb | Yes | 70 | TMS | CWW22_9 | S40841/1 (PR24 Hybrid air source heat pump/existing boiler for 4 corporate offices (Waste)) | Feasible | 0.605 | 0.529 | -0.054 | -0.037 | -0.025 | 1.018 | -198.77 | -596.3 | -993.83 | -1391.36 | -1788.89 | -1788.89 | Rejected at DD: company representation.
TMS-DD-002-PR24-Draft-Determination-Data-Tables.xlsb | Yes | 71 | TMS | CWW22_10 | S40842/2 (PR24 Air source heat pump for site office (enhancement cost) (Waste)) | Feasible | 0.506 | 0.525 | 0.546 | 0.567 | 0.591 | 2.735 | -50 | -150.019 | -300.038 | -500.067 | -750.066 | -750.066 | Rejected at DD: company representation.
24 09 16 - UUW BPDTS.xlsb | No | 72 | NWT | E00001337 | Stationary fossil fuel reductions | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rejected at DD, no company representation.
24 09 16 - UUW BPDTS.xlsb | No | 73 | NWT | E00001338 | Process emissions (Bioresources) | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rejected at DD: no company representation.
24 09 16 - UUW BPDTS.xlsb | Yes | 74 | NWT | E00001339 | Process emissions (Wastewater) | Selected | 27.2204 | 1.6984 | 1.7133 | 1.7119 | 1.7604 | 34.1044 | 0 | 0 | -12541.041 | -37623.123 | -62705.206 | -62705.206 | Rejected at DD: company representation.
24 09 16 - UUW BPDTS.xlsb | Yes | 75 | NWT | E00001340 | Transport fossil fuel reductions - Green fleet LCVs phase 1 | Selected | 1.5426 | 1.6035 | 3.0676 | 1.8107 | -2.2169 | 5.8076 | -338 | -1438 | -3807 | -7739 | -12389 | -12389 | Rejected at DD: company representation.
24 09 16 - UUW BPDTS.xlsb | No | 76 | NWT | E00001341 | Transport fossil fuel reductions - Green fleet LCVs phase 2 | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rejected at DD: no company representation.
24 09 16 - UUW BPDTS.xlsb | Yes | 77 | NWT | E00001342 | Transport fossil fuel reductions - Green fleet Biomethane HGVs | Selected | 0.29427 | 0.27235 | 0.24384 | 0.22063 | 0.19319 | 1.2243 | -155 | -619 | -1392 | -2474 | -3866 | -3866 | Rejected at DD: company representation.
24 09 16 - UUW BPDTS.xlsb | No | 78 | NWT | E00001426 | Phase 2 – Further low regrets emissions reductions in AMP8 | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rejected at DD: no company representation.
24 09 16 - UUW BPDTS.xlsb | No | 79 | NWT | E00001346 | Property emissions reductions | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rejected at DD: no company representation.
24 09 16 - UUW BPDTS.xlsb | Yes | 80 | NWT | E00001425 | Net zero catchment strategy | Selected | 0.50404 | 0.25636 | 0.15266 | 0.10336 | 0 | 1.0164 | 0 | 0 | 0 | 0 | 0 |  | Approved at DD and included in company representation response to DD.
WSH-DD-101 PR24 Business Plan tables V7_Amended 240917.xlsb | Yes | 81 | WSH | CWW22_1 | Net Zero Carbon Strategy: Network Control Systems (Wastewater) | Selected | 0.12931 | 0.28986 | 0.28938 | 0.30456 | 0.2576 | 1.2707 | -50 | -165 | -285 | -400 | -500 | -500 | Rejected at DD: company representation.
WSH-DD-101 PR24 Business Plan tables V7_Amended 240917.xlsb | Yes | 82 | WSH | CWW22_2 | Net Zero Carbon Strategy: Reduction of Process Emissions | Selected | 6.3079 | 7.2758 | 7.2641 | 7.3845 | 7.1256 | 35.358 | -10045 | -13831.5 | -16453 | -18157 | -19372 | -19372 | Rejected at DD: company representation.
WSX-D00a – August 2024 data tables v8. WORKING VERSION POST-DD 12.09.24.xlsx | Yes | 83 | WSX | CWW22_1 | Heat recovery | Selected | 1.0792 | -1.1834 | -1.1893 | -1.1952 | -1.2012 | -3.6899 |  | -729.8 | -729.8 | -729.8 | -729.8 | -729.8 | Rejected at DD: company representation.
WSX-D00a – August 2024 data tables v8. WORKING VERSION POST-DD 12.09.24.xlsx | Yes | 84 | WSX | CWW22_2 | Nitrous oxide - standard enhancement | Selected | 0 | 0 | 0.61354 | 0.1187 | 0.11929 | 0.85153 |  |  | -652.74 | -1305.5 | -1978 | -1978 | Rejected at DD: company representation.
WSX-D00a – August 2024 data tables v8. WORKING VERSION POST-DD 12.09.24.xlsx | Yes | 85 | WSX | CWW22_3 | Nitrous oxide - NZ challenge | Selected | 0.74424 | 0.11752 | 0.29789 | 0.10469 | 0.10521 | 1.3695 |  |  | -294.492 | -589 | -892.4 | -892.4 | Rejected at DD: company representation.
WSX-D00a – August 2024 data tables v8. WORKING VERSION POST-DD 12.09.24.xlsx | Yes | 86 | WSX | CWW22_4 | Transport | Selected | 0.92105 | 1.4813 | 1.8663 | 1.8793 | 0.98255 | 7.1305 | -196 | -588 | -176 | -1961 | -2941 | -2941 | Rejected at DD: company representation.
WSX-D00a – August 2024 data tables v8. WORKING VERSION POST-DD 12.09.24.xlsx | Yes | 87 | WSX | CWW22_5 | On-site renewables | Feasible | 0 | 0 | 0 | 0 | 3.9 | 3.9 |  |  | -1752 | -3504 | -5256 | -5256 | Rejected at DD: company representation.
WSX-D00a – August 2024 data tables v8. WORKING VERSION POST-DD 12.09.24.xlsx | Yes | 88 | WSX | CWW22_6 | Exported heat | Feasible | 0 | 0 | 0 | 2.4271 | -0.1458 | 2.2813 |  |  | -1213.35 | -2426.7 | -3640.05 | -3640.05 | Rejected at DD: company representation.
YKY-PR24-DDR-85-Data-Tables-18Sept24_coastal.xlsb | No | 89 | YKY | CWW22-1 | Solar | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rejected at DD: no company representation.
YKY-PR24-DDR-85-Data-Tables-18Sept24_coastal.xlsb | Yes | 90 | YKY | CWW22-2 | Methane reduction | Selected | 3.287 | 6.168 | 0.185 | 0.185 | 0.184 | 10.009 | 0 | -5397 | -19300 | -27806 | -41709 | -41709 | Rejected at DD: company representation.
YKY-PR24-DDR-85-Data-Tables-18Sept24_coastal.xlsb | Yes | 91 | YKY | CWW22-3 | Nitrous oxide reduction | Selected | 5.693 | 3.875 | 1.211 | 1.211 | 1.211 | 13.201 | 0 | -2500 | -7000 | -9918 | -16254 | -16254 | Rejected at DD: company representation.
This data is taken from business plan table CWW22 submitted as part of company representations on Draft Determinations submitted in August/September 2024. Schemes that were not resubmitted are presented in strike-through and indicated in column B. Where data has changed due to a query response, this is indicated in column U.

## Data Final
#VALUE!
Scheme resubmitted at DD | No. | Company | Scheme ID | Scheme name | Selected or Feasible | Totex 2025-26 | Totex 2026-27 | Totex 2027-28 | Totex 2028-29 | Totex 2029-30 | AMP8 totex (£m, 2025-30) | Carbon benefits (cumulated) 2025-26 | Carbon benefits (cumulated) 2026-27 | Carbon benefits (cumulated) 2027-28 | Carbon benefits (cumulated) 2028-29 | Carbon benefits (cumulated) 2029-30 | Scheme benefits (tCO2e cumulative, 2029-30) | Unit cost over AMP8 (000£/tCO2e) | Unit cost over AMP8 (£/tCO2e) | Final Decision
Yes | 1 | ANH | CWW22.1 | Cotton Valley STC - Centrate quality | Selected | 0 | 0.48865 | 3.4843 | 6.126 | 4.5286 | 14.6275 | 0 | 0 | 0 | 0 | -287.5 | -287.5 | 50.8783 | 50878.3091 | Pass
No | 2 | ANH | CWW22.2 | Cotton Valley STC gas to grid | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | Fail
No | 3 | ANH | CWW22.3 | Great Billing STC gas to grid | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | Fail
No | 4 | ANH | CWW22.4 | Cotton Valley STC Fugitive emissions CH4 | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | Fail
No | 5 | ANH | CWW22.5 | Whitlingham STC Gas to Grid (AMP8) | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | Fail
No | 6 | ANH | CWW22.6 | Great Billing STC Fugitive emissions CH4 | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | Fail
No | 7 | ANH | CWW22.7 | Whitlingham STC Fugitive emissions CH4 | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | Fail
No | 8 | ANH | CWW22.8 | Cliff Quay STC Fugitive Emissions CH4 | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | Fail
No | 9 | ANH | CWW22.9 | Pyewipe STC Fugitive emissions CH4 | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | Fail
No | 10 | ANH | CWW22.10 | Colchester STC Fugitive emissions CH4 | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | Fail
No | 11 | ANH | CWW22.11 | Basildon STC Fugitive emissions CH4 | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | Fail
No | 12 | ANH | CWW22.12 | Kings Lynn STC Fugitive emissions CH4 | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | Fail
No | 13 | ANH | CWW22.13 | Cotton Valley WRC Fugitive emissions CH4 | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | Fail
Yes | 14 | ANH | CWW22.14 | Basildon STC Fugitive emissions N2O | Selected | 0 | 0 | 0.30472 | 0.71523 | 0.53552 | 1.5555 | 0 | 0 | 0 | 0 | -174 | -174 | 8.9395 | 8939.4998 | Pass
Yes | 15 | ANH | CWW22.15 | Colchester STC Fugitive emissions N2O | Selected | 0.28658 | 0.57316 | 0.5807 | 0.010084 | 0.020609 | 1.4711 | 0 | 0 | -116 | -348 | -580 | -580 | 2.5364 | 2536.4313 | Pass
Yes | 16 | ANH | CWW22.16 | Cliff Quay STC Fugitive emissions N2O | Selected | 0 | 0 | 0.31847 | 0.63695 | 0.64461 | 1.6 | 0 | 0 | 0 | 0 | -273 | -273 | 5.8609 | 5860.9263 | Pass
Yes | 17 | ANH | CWW22.17 | Whitlingham STC Fugitive Emissions N2O | Selected | 0 | 0 | 0.13846 | 0.27691 | 0.28579 | 0.70116 | 0 | 0 | 0 | 0 | -215 | -215 | 3.2612 | 3261.215 | Fail
Yes | 18 | ANH | CWW22.18 | Cotton Valley WRC Fugitive emissions N2O | Selected | 0.34027 | 0.68053 | 0.68053 | 0 | 0 | 1.7013 | 0 | 0 | -35.417 | -460.417 | -885.417 | -885.417 | 1.9215 | 1921.5 | Pass
Yes | 19 | ANH | CWW22.19 | Great Billing WRC Fugitive Emissions N2O | Selected | 0 | 0.41339 | 0.82677 | 0.82692 | 0.000274 | 2.0673 | 0 | 0 | 0 | -34.65 | -450.45 | -450.45 | 4.5895 | 4589.5097 | Pass
Yes | 20 | ANH | CWW22.20 | Basildon WRC Fugitive Emissions N2O | Selected | 0 | 0.12178 | 0.49044 | 0.74134 | 0.40749 | 1.7611 | 0 | 0 | 0 | -42.85 | -214.25 | -214.25 | 8.2196 | 8219.613 | Pass
Yes | 21 | ANH | CWW22.21 | Bedford WRC Fugitive Emissions N2O | Selected | 0 | 0.03742 | 0.1871 | 0.29938 | 0.22459 | 0.74849 | 0 | 0 | 0 | -63.05 | -315.25 | -315.25 | 2.3743 | 2374.2627 | Pass
Yes | 22 | ANH | CWW22.22 | Kings Lynn WRC Fugitive Emissions N2O | Selected | 0.19039 | 0.38078 | 0.38078 | 0 | 0 | 0.95194 | 0 | 0 | -44.3 | -132.9 | -221.5 | -221.5 | 4.2977 | 4297.7103 | Pass
Yes | 23 | ANH | CWW22.23 | Newton Marsh WRC Fugitive Emissions N2O | Selected | 0 | 0 | 0.089361 | 0.17872 | 0.17872 | 0.4468 | 0 | 0 | 0 | 0 | -72.5 | -72.5 | 6.1628 | 6162.7945 | Pass
Yes | 24 | ANH | CWW22.24 | Broadholme WRC Fugitive Emissions N2O | Selected | 0.16084 | 0.28268 | 0.20442 | 0 | 0 | 0.64794 | 0 | 0 | -10.408 | -135.308 | -260.208 | -260.208 | 2.4901 | 2490.0776 | Pass
Yes | 25 | ANH | CWW22.25 | Letchworth WRC Fugitive emissions N2O | Selected | 0 | 0.88886 | 2.5194 | 4.586 | 3.3527 | 11.3471 | 0 | 0 | 0 | 0 | -127.6 | -127.6 | 88.9268 | 88926.7971 | Pass
Yes | 26 | ANH | CWW22.26 | Newmarket WRC Fugitive Emissions N2O | Selected | 0 | 0 | 0.91948 | 1.839 | 1.8498 | 4.6082 | 0 | 0 | 0 | 0 | -26.5 | -26.5 | 173.8945 | 173894.5494 | Pass
Yes | 27 | ANH | CWW22.27 | Hitchin WRC Fugitive emissions N2O | Selected | 0 | 0.052293 | 0.20917 | 0.31376 | 0.20917 | 0.7844 | 0 | 0 | 0 | -12.675 | -63.375 | -32.95 | 23.8057 | 23805.7311 | Pass
Yes | 28 | ANH | CWW22.28 | Dunstable WRC Fugitive Emissions N2O | Selected | 0 | 0.95962 | 2.72 | 4.9511 | 3.6432 | 12.274 | 0 | 0 | 0 | 0 | -75.3 | -75.3 | 163.0011 | 163001.1076 | Pass
Yes | 29 | ANH | CWW22.29 | Flitwick WRC Fugitive Emissions N2O | Selected | 0.52737 | 1.4682 | 2.5719 | 1.7562 | 0.097275 | 6.4209 | 0 | 0 | -3.532 | -51.214 | -139.514 | -139.514 | 46.0234 | 46023.4063 | Pass
No | 30 | ANH | CWW22.30 | Great Billing STC Liquor Ammonia | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | Fail
No | 31 | ANH | CWW22.31 | Logistics Fleet CO2 emissions 2025-26 | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | Fail
No | 32 | ANH | CWW22.32 | Logistics fleet CO2 emissions 2026-27 | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | Fail
No | 33 | ANH | CWW22.33 | Logistics fleet CO2 emissions 2027-28 | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | Fail
No | 34 | ANH | CWW22.34 | Logistics fleet CO2 emissions 2028-29 | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | Fail
No | 35 | ANH | CWW22.35 | Logistics fleet CO2 emissions 2029-30 | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | Fail
Yes | 36 | ANH | CWW22.36 | Huntingdon WRC Fugitive Emissions N2O | Selected | 0 | 0 | 0 | 0.17376 | 0.35927 | 0.53303 | 0 | 0 | 0 | 0 | -60.2 | -60.2 | 8.8543 | 8854.2678 | Pass
No | 37 | ANH | CWW22.37 | AMP8 Small Scale Solar Delivery WR | Feasible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | Fail
No | 38 | ANH | CWW22.38 | Basildon STC Gas to Grid | Feasible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | Fail
No | 39 | ANH | CWW22.39 | Colchester STC Gas to Grid | Feasible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | Fail
No | 40 | ANH | CWW22.40 | Ipswich Cliff Quay STC Gas to Grid | Feasible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | Fail
No | 41 | ANH | CWW22.41 | Pyewipe STC Gas to Grid | Feasible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | Fail
No | 42 | ANH | CWW22.42 | Kings Lynn STC gas to grid | Feasible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | Fail
No | 43 | ANH | CWW22.43 | Whitlingham WRC Fugitive Emissions N2O | Feasible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | Fail
No | 44 | ANH | CWW22.44 | Colchester WRC Fugitive Emissions N2O | Feasible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | Fail
Yes | 45 | ANH | CWW22.45 | Colchester WRC Fugitive Emissions N2O | Feasible | 0.93235 | 2.6427 | 4.8104 | 3.531 | 0.041357 | 11.958 | 0 | 0 | -264.7 | -22.058 | -286.758 | -286.758 | 41.7007 | 41700.6675 | Pass
Yes | 46 | HDD | CWW22.1 | Process Emissions Reduction | Selected | 0.49147 | 0.29561 | 0.025488 | 0.025488 | 0.025488 | 0.86355 | 0 | 0 | -137.13 | -274.265 | -411.3975 | -411.398 | 2.0991 | 2099.0622 | Pass
No | 47 | HDD | CWW22.2 | Heat Decarbonisation | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | Fail
Yes | 48 | SVE | NZ#1 | Digital Twin | Selected | 12.786 | 25.571 | -2.118 | 8.551 | 8.551 | 53.341 | 0 | 0 | -1400 | -4300 | -8600 | -8600 | 6.2024 | 6202.4419 | Pass
Yes | 49 | SVE | NZ#2 | Cover & Treat | Selected | 18.579 | 18.579 | 18.579 | 18.579 | 18.579 | 92.895 | 0 | 0 | -7607.71 | -23251.86 | -74239.11 | -74239.11 | 1.2513 | 1251.2946 | Pass
Yes | 50 | SVE | NZ#3 | ASP Intensification | Selected | 4.076 | 28.561 | 25.891 | 23.954 | 21.629 | 104.111 | 0 | 0 | -8326.56 | -24979.68 | -49959.36 | -49959.36 | 2.0839 | 2083.9138 | Pass
Yes | 51 | SVE | NZ#4 | Active gas capture | Selected | 0 | 0 | 12.948 | 8.714 | 13.959 | 35.621 | 0 | 0 | -1359 | -4078 | -8156 | -13593 | 2.6205 | 2620.54 | Pass
Yes | 52 | SVE | NZ#5 | EV Charging Infrastructure | Selected | 0 | 0.72 | 0 | 0 | 0 | 0.72 | 0 | 0 | -311.4 | -934.2 | -1868.4 | -1868.4 | 0.38536 | 385.3565 | Fail
Yes | 53 | SVE | NZ#6 | Heat pumps | Selected | 6.598 | 0 | -0.06 | -0.09 | -0.09 | 6.358 | 0 | 0 | -209.25 | -627.75 | -1255.5 | -1255.5 | 5.0641 | 5064.1179 | Fail
Yes | 54 | SVE | NZ#7 | HVO diesel replacement | Selected | 0.271 | 0 | 0 | 0 | 0 | 0.271 | 0 | 0 | -567 | -1701 | -3402 | -3402 | 0.079659 | 79.659 | Fail
Yes | 55 | SVE | NZ#8 | Cellulose recovery | Selected | 0 | 0 | 31.772 | 31.772 | -0.469 | 63.075 | 0 | 0 | -1516.8 | -7810.4 | -15620.8 | -15620.8 | 4.0379 | 4037.8854 | Fail
Yes | 56 | SVE | NZ#9 | Process Optimisation | Selected | 6.045 | 0 | 0.738 | 1.092 | 1.092 | 8.967 | 0 | 0 | -8200 | -16400 | -24600 | -24600 | 0.36451 | 364.5122 | Pass
Yes | 57 | SVE | NZ#10 | Hydrogen Production | Feasible | 0.45 | 0.45 | 0.237 | 0.237 | 0.237 | 1.611 | 0 | 0 | -806.4 | -1612.8 | -2419.2 | -2419.2 | 0.66592 | 665.9226 | Fail
Yes | 58 | SVE | NZ#11 | Electrical storage | Feasible | 0.99 | 0.99 | 0.577 | 0.577 | 0.577 | 3.711 | 0 | 0 | -32.85 | -65.7 | -98.55 | -98.55 | 37.656 | 37656.0122 | Fail
Yes | 59 | SVE | NZ#12 | EV fleet only | Feasible | 0.657 | 0.657 | 0.657 | 0.657 | 0.657 | 3.285 | 0 | 0 | -1557 | -3114 | -4671 | -4671 | 0.70328 | 703.2755 | Fail
Yes | 60 | SVE | NZ#13 | HVO fuel only | Feasible | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 1.8 | -2271.6 | -4543.2 | -6814.8 | -9086.4 | -11358 | -11358 | 0.15848 | 158.4786 | Fail
Yes | 61 | SVE | NZ#14 | Solar PV | Feasible | 2.34 | 2.34 | -0.285 | -0.285 | -0.285 | 3.825 | 0 | 0 | -2625.37 | -5250.74 | -7876.12 | -7876.12 | 0.48565 | 485.6452 | Fail
Yes | 62 | TMS | CWW22_1 | S40749/1 (Long Reach - Installation of Biomethane Plant - Delta from botex for bidding process) | Feasible | 5.886 | 3.747 | 2.985 | 3.018 | 3.186 | 18.822 | 0 | 0 | -2537.57 | -5075.14 | -7612.71 | -7612.71 | 2.4724 | 2472.4441 | Fail
Yes | 63 | TMS | CWW22_2 | Aylesbury - Installation of Biomethane Plant with heat pump - Delta from botex for bidding process | Feasible | 0 | 1.107 | 0.371 | 0.472 | 0.5 | 2.45 | 0 | 0 | 0 | -476.348 | -952.697 | -952.697 | 2.5716 | 2571.6466 | Fail
Yes | 64 | TMS | CWW22_3 | Bishop Stortford - Installation of Biomethane Plant - enhancement from botex for bidding process | Feasible | 0 | 0 | 0 | 0.355 | 0.258 | 0.613 | 0 | 0 | 0 | -290.137 | -581.009 | -581.009 | 1.0551 | 1055.0611 | Fail
Yes | 65 | TMS | CWW22_4 | Didcot - Installation of Biomethane Plant - enhancement from botex for bidding process | Feasible | 0 | 0.1 | 0.112 | 0.115 | 0.126 | 0.453 | 0 | -369.425 | -677.409 | -985.392 | -1293.376 | -1293.376 | 0.35025 | 350.2462 | Fail
Yes | 66 | TMS | CWW22_5 | East Hyde - Installation of Biomethane Plant - enhancement from botex for bidding process | Feasible | 0 | 0 | 0 | 0.519 | 0.555 | 1.074 | 0 | 0 | 0 | -558.252 | -1116.504 | -1116.504 | 0.96193 | 961.9312 | Fail
Yes | 67 | TMS | CWW22_6 | Hogsmill -Installation of Biomethane Plant - enhancement from botex for bidding process | Feasible | 0 | 1.777 | 1.185 | 1.239 | 1.303 | 5.504 | 0 | 0 | 0 | -1109.173 | -2219.814 | -2219.814 | 2.4795 | 2479.487 | Fail
Yes | 68 | TMS | CWW22_7 | Reading - Installation of Biomethane Plant - enhancement from botex for bidding process | Feasible | 0 | 0 | 0 | 0.923 | 1.044 | 1.967 | 0 | 0 | 0 | -1040.033 | -2138.606 | -2138.606 | 0.91976 | 919.758 | Fail
Yes | 69 | TMS | CWW22_8 | S40040/4 (PR24 Fleet - Life expired Enhancement (cost to convert to electrical) (Waste)) | Feasible | 6.717 | 6.028 | 4.727 | 3.199 | 0.139 | 20.81 | -1212 | -3150 | -5770 | -9140 | -13142 | -13142 | 1.5835 | 1583.4728 | Fail
Yes | 70 | TMS | CWW22_9 | S40841/1 (PR24 Hybrid air source heat pump/existing boiler for 4 corporate offices (Waste)) | Feasible | 0.605 | 0.529 | -0.054 | -0.037 | -0.025 | 1.018 | -198.77 | -596.3 | -993.83 | -1391.36 | -1788.89 | -1788.89 | 0.56907 | 569.068 | Fail
Yes | 71 | TMS | CWW22_10 | S40842/2 (PR24 Air source heat pump for site office (enhancement cost) (Waste)) | Feasible | 0.506 | 0.525 | 0.546 | 0.567 | 0.591 | 2.735 | -50 | -150.019 | -300.038 | -500.067 | -750.066 | -750.066 | 3.6463 | 3646.3458 | Fail
No | 72 | NWT | E00001337 | Stationary fossil fuel reductions | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | Fail
No | 73 | NWT | E00001338 | Process emissions (Bioresources) | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | Fail
Yes | 74 | NWT | E00001339 | Process emissions (Wastewater) | Selected | 27.2204 | 1.6984 | 1.7133 | 1.7119 | 1.7604 | 34.1044 | 0 | 0 | -12541.041 | -37623.123 | -62705.206 | -62705.206 | 0.54388 | 543.8848 | Pass
Yes | 75 | NWT | E00001340 | Transport fossil fuel reductions - Green fleet LCVs phase 1 | Selected | 1.5426 | 1.6035 | 3.0676 | 1.8107 | -2.2169 | 5.8076 | -338 | -1438 | -3807 | -7739 | -12389 | -12389 | 0.46877 | 468.7707 | Fail
No | 76 | NWT | E00001341 | Transport fossil fuel reductions - Green fleet LCVs phase 2 | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | Fail
Yes | 77 | NWT | E00001342 | Transport fossil fuel reductions - Green fleet Biomethane HGVs | Selected | 0.29427 | 0.27235 | 0.24384 | 0.22063 | 0.19319 | 1.2243 | -155 | -619 | -1392 | -2474 | -3866 | -3866 | 0.31668 | 316.6767 | Fail
No | 78 | NWT | E00001426 | Phase 2 – Further low regrets emissions reductions in AMP8 | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | Fail
No | 79 | NWT | E00001346 | Property emissions reductions | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | Fail
Yes | 80 | NWT | E00001425 | Net zero catchment strategy | Selected | 0.50404 | 0.25636 | 0.15266 | 0.10336 | 0 | 1.0164 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | Pass
Yes | 81 | WSH | CWW22_1 | Net Zero Carbon Strategy: Network Control Systems (Wastewater) | Selected | 0.12931 | 0.28986 | 0.28938 | 0.30456 | 0.2576 | 1.2707 | -50 | -165 | -285 | -400 | -500 | -500 | 2.5414 | 2541.4254 | Fail
Yes | 82 | WSH | CWW22_2 | Net Zero Carbon Strategy: Reduction of Process Emissions | Selected | 6.3079 | 7.2758 | 7.2641 | 7.3845 | 7.1256 | 35.358 | -10045 | -13831.5 | -16453 | -18157 | -19372 | -19372 | 1.8252 | 1825.2094 | Pass
Yes | 83 | WSX | CWW22_1 | Heat recovery | Selected | 1.0792 | -1.1834 | -1.1893 | -1.1952 | -1.2012 | -3.6899 | 0 | -729.8 | -729.8 | -729.8 | -729.8 | -729.8 | 5.0561 | 5056.1111 | Fail
Yes | 84 | WSX | CWW22_2 | Nitrous oxide - standard enhancement | Selected | 0 | 0 | 0.61354 | 0.1187 | 0.11929 | 0.85153 | 0 | 0 | -652.74 | -1305.5 | -1978 | -1978 | 0.4305 | 430.5029 | Pass
Yes | 85 | WSX | CWW22_3 | Nitrous oxide - NZ challenge | Selected | 0.74424 | 0.11752 | 0.29789 | 0.10469 | 0.10521 | 1.3695 | 0 | 0 | -294.492 | -589 | -892.4 | -892.4 | 1.5347 | 1534.6787 | Pass
Yes | 86 | WSX | CWW22_4 | Transport | Selected | 0.92105 | 1.4813 | 1.8663 | 1.8793 | 0.98255 | 7.1305 | 0 | 0 | 0 | 0 | 0 | -2941 | 2.4245 | 2424.5196 | Fail
Yes | 87 | WSX | CWW22_5 | On-site renewables | Feasible | 0 | 0 | 0 | 0 | 3.9 | 3.9 | 0 | 0 | -1752 | -3504 | -5256 | -5256 | 0.74201 | 742.0091 | Fail
Yes | 88 | WSX | CWW22_6 | Exported heat | Feasible | 0 | 0 | 0 | 2.4271 | -0.1458 | 2.2813 | 0 | 0 | -1213.35 | -2426.7 | -3640.05 | -3640.05 | 0.62672 | 626.7222 | Fail
No | 89 | YKY | CWW22-1 | Solar | Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | Fail
Yes | 90 | YKY | CWW22-2 | Methane reduction | Selected | 3.287 | 6.168 | 0.185 | 0.185 | 0.184 | 10.009 | 0 | -5397 | -19300 | -27806 | -41709 | -41709 | 0.23997 | 239.9722 | Pass
Yes | 91 | YKY | CWW22-3 | Nitrous oxide reduction | Selected | 5.693 | 3.875 | 1.211 | 1.211 | 1.211 | 13.201 | 0 | -2500 | -7000 | -9918 | -16254 | -16254 | 0.81217 | 812.1693 | Pass
|  |  |  | Total | 91 | [5 empty] | 625.9407 | [5 empty] | -428498.463 | 1.4608 | 1460.7769

## Phase 1 - Initial Assessment
#VALUE!
Is the scheme true enhancement, a core business activity and has the reduction of GHG emissions as its primary driver?
| Scheme submitted | [5 empty] | Enhancement expenditure |  | Net zero as the primary driver |  | Core business activity |  | Decisions of phase 1 |  | Results of phase 1
|  | Company | Scheme ID | Scheme name | Scheme description | Category | Was this activity previously delivered by base expenditure? (Yes/No) | Justification | Is net zero the primary driver of the scheme? (Yes/No) | Justification | Is the scheme a core business activity? (Yes/No) | Justification | Phase 1 assessment decision (pass/fail) | Rationale |  | Company | Scheme ID | Scheme name
| 1 | ANH | CWW22.1 | Cotton Valley STC - Centrate quality | Liquor recovery - Installation of Ammonia stripping and recovery into liquid Ammonium Sulphate. The cost includes the up and downstream pumping of flows to the recovery plant, product storage and loading facilities. | Process emissions | No | This is process is to capture and mitigate N2O from liquor treatment | Yes | N2O emissions reductions from liquor treatment primary driver | Yes |  | Pass | Net Zero from N2O reductions primary driver, no wider benefit | 1 | ANH | CWW22.1 | Cotton Valley STC - Centrate quality
| 2 | ANH | CWW22.2 | Cotton Valley STC gas to grid | Converting CHP engines at end of life to permit to inject into gas network. | Gas to grid | No | Gas to grid delivered under base expenditure for 2020-2025. | Yes | Carbon benefit but also revenue generating scheme | No |  | Fail | Should continue to be funded by Base expenditure | 2
| 3 | ANH | CWW22.3 | Great Billing STC gas to grid | Converting CHP engines at end of life to permit to inject into gas network. | Gas to grid | No | Gas to grid delivered under base expenditure for 2020-2025. | Yes | Carbon benefit but also revenue generating scheme | No |  | Fail | Should continue to be funded by Base expenditure | 3
| 4 | ANH | CWW22.4 | Cotton Valley STC Fugitive emissions CH4 | Interventions for Advanced Anaerobic Digesters at eight Sludge Treatment Centres (STC). The technology is a combination of different methods to maximise collection of methane, minimise leakage. Containment of the emissions. Covering of open digester limpet chambers to entrain gas. Vacuum degassing of the digestate and connection to the gas header. Covering of the post digestion storage tank, with appropriate safety systems to prevent over pressurisation of these tanks and connection to the gas header. Replacement of the post digestion aeration system with gas mixing and the installation of a final stage of flash aeration (covered and odour controlled) prior to dewatering. | Process emissions | No | Maintenance of assets under base. Spend to save (commercial opportunity from methane collection) not provided for in base. | Yes | Methane capture in the bioresources stage of wastewater treatment is the primary driver. This is driven by Net Zero but could also be driven by IED | No |  | Fail | Methane capture creates commercial opportunity. Industrial Emissions Directive methane requirement. | 4
| 5 | ANH | CWW22.5 | Whitlingham STC Gas to Grid (AMP8) | Converting CHP engines at end of life to permit to inject into gas network. | Gas to grid | No | Gas to grid delivered under base expenditure for 2020-2025. | Yes | Carbon benefit but also revenue generating scheme | No |  | Fail | Should continue to be funded by Base expenditure | 5
| 6 | ANH | CWW22.6 | Great Billing STC Fugitive emissions CH4 | Interventions for Advanced Anaerobic Digesters at eight Sludge Treatment Centres (STC). The technology is a combination of different methods to maximise collection of methane, minimise leakage, optimise connection of methane generating plant to the biogas system. Extraction of methane by vacuum degassing. Containment of the emissions. | Process emissions | No | Maintenance of assets under base. Spend to save (commercial opportunity from methane collection) not provided for in base. | Yes | Methane capture in the bioresources stage of wastwater treatment is the primary driver. This is driven by Net Zero but could also be driven by IED | No |  | Fail | Methane capture creates commercial opportunity. Industrial Emissions Directive methane requirement | 6
| 7 | ANH | CWW22.7 | Whitlingham STC Fugitive emissions CH4 | Interventions for Advanced Anaerobic Digesters at eight Sludge Treatment Centres (STC). The technology is a combination of different methods to maximise collection of methane, minimise leakage, optimise connection of methane generating plant to the biogas system. Extraction of methane by vacuum degassing. Containment of the emissions. | Process emissions | No | Maintenance of assets under base. Spend to save (commercial opportunity from methane collection) not provided for in base. | Yes | Methane capture in the bioresources stage of wastwater treatment is the primary driver. This is driven by Net Zero but could also be driven by IED | No |  | Fail | Methane capture creates commercial opportunity. Industrial Emissions Directive methane requirement | 7
| 8 | ANH | CWW22.8 | Cliff Quay STC Fugitive Emissions CH4 | Interventions for Advanced Anaerobic Digesters at eight Sludge Treatment Centres (STC). The technology is a combination of different methods to maximise collection of methane, minimise leakage, optimise connection of methane generating plant to the biogas system. Extraction of methane by vacuum degassing. Containment of the emissions. | Process emissions | No | Maintenance of assets under base. Spend to save (commercial opportunity from methane collection) not provided for in base. | Yes | Methane capture in the bioresources stage of wastwater treatment is the primary driver. This is driven by Net Zero but could also be driven by IED | No |  | Fail | Methane capture creates commercial opportunity. Industrial Emissions Directive methane requirement | 8
| 9 | ANH | CWW22.9 | Pyewipe STC Fugitive emissions CH4 | Interventions for Advanced Anaerobic Digesters at eight Sludge Treatment Centres (STC). The technology is a combination of different methods to maximise collection of methane, minimise leakage, optimise connection of methane generating plant to the biogas system. Extraction of methane by vacuum degassing. Containment of the emissions. | Process emissions | No | Maintenance of assets under base. Spend to save (commercial opportunity from methane collection) not provided for in base. | Yes | Methane capture in the bioresources stage of wastwater treatment is the primary driver. This is driven by Net Zero but could also be driven by IED | No |  | Fail | Methane capture creates commercial opportunity. Industrial Emissions Directive methane requirement | 9
| 10 | ANH | CWW22.10 | Colchester STC Fugitive emissions CH4 | Interventions for Advanced Anaerobic Digesters at eight Sludge Treatment Centres (STC). The technology is a combination of different methods to maximise collection of methane, minimise leakage, optimise connection of methane generating plant to the biogas system. Extraction of methane by vacuum degassing. Containment of the emissions. | Process emissions | No | Maintenance of assets under base. Spend to save (commercial opportunity from methane collection) not provided for in base. | Yes | Methane capture in the bioresources stage of wastwater treatment is the primary driver. This is driven by Net Zero but could also be driven by IED | No |  | Fail | Methane capture creates commercial opportunity. Industrial Emissions Directive methane requirement | 10
| 11 | ANH | CWW22.11 | Basildon STC Fugitive emissions CH4 | Interventions for Advanced Anaerobic Digesters at eight Sludge Treatment Centres (STC). The technology is a combination of different methods to maximise collection of methane, minimise leakage, optimise connection of methane generating plant to the biogas system. Extraction of methane by vacuum degassing. Containment of the emissions. | Process emissions | No | Maintenance of assets under base. Spend to save (commercial opportunity from methane collection) not provided for in base. | Yes | Methane capture in the bioresources stage of wastwater treatment is the primary driver. This is driven by Net Zero but could also be driven by IED | No |  | Fail | Methane capture creates commercial opportunity. Industrial Emissions Directive methane requirement | 11
| 12 | ANH | CWW22.12 | Kings Lynn STC Fugitive emissions CH4 | Interventions for Advanced Anaerobic Digesters at eight Sludge Treatment Centres (STC). The technology is a combination of different methods to maximise collection of methane, minimise leakage, optimise connection of methane generating plant to the biogas system. Extraction of methane by vacuum degassing. Containment of the emissions. | Process emissions | No | Maintenance of assets under base. Spend to save (commercial opportunity from methane collection) not provided for in base. | Yes | Methane capture in the bioresources stage of wastwater treatment is the primary driver. This is driven by Net Zero but could also be driven by IED | No |  | Fail | Methane capture creates commercial opportunity. Industrial Emissions Directive methane requirement | 12
| 13 | ANH | CWW22.13 | Cotton Valley WRC Fugitive emissions CH4 | Interventions for Advanced Anaerobic Digesters at eight Sludge Treatment Centres (STC). The technology is a combination of different methods to maximise collection of methane, minimise leakage, optimise connection of methane generating plant to the biogas system. Extraction of methane by vacuum degassing. Containment of the emissions. | Process emissions | No | Maintenance of assets under base. Spend to save (commercial opportunity from methane collection) not provided for in base. | Yes | Methane capture in the bioresources stage of wastwater treatment is the primary driver. This is driven by Net Zero but could also be driven by IED | No |  | Fail | Methane capture creates commercial opportunity. Industrial Emissions Directive methane requirement | 13
| 14 | ANH | CWW22.14 | Basildon STC Fugitive emissions N2O | Contain and treat - Covering and odour control of the anoxic and aeration tanks on the Amtreat plant. | Process emissions | No | Expenditure to cover assets to capture emissions not requested for 2020-2025 | Yes | Capture of N2O for no other purpose but to prevent emission | Yes |  | Pass | Net Zero primary driver | 14 | ANH | CWW22.14 | Basildon STC Fugitive emissions N2O
| 15 | ANH | CWW22.15 | Colchester STC Fugitive emissions N2O | Contain and treat - Covering and odour control of the anoxic and aeration tanks on the Amtreat plant. | Process emissions | No | Expenditure to cover assets to capture emissions not requested for 2020-2025 | Yes | Capture of N2O for no other purpose but to prevent emission | Yes |  | Pass | Net Zero primary driver | 15 | ANH | CWW22.15 | Colchester STC Fugitive emissions N2O
| 16 | ANH | CWW22.16 | Cliff Quay STC Fugitive emissions N2O | Contain and treat - Covering and odour control of the anoxic and aeration tanks on the Amtreat plant. | Process emissions | No | Expenditure to cover assets to capture emissions not requested for 2020-2025 | Yes | Capture of N2O for no other purpose but to prevent emission | Yes |  | Pass | Net Zero primary driver | 16 | ANH | CWW22.16 | Cliff Quay STC Fugitive emissions N2O
| 17 | ANH | CWW22.17 | Whitlingham STC Fugitive Emissions N2O | Contain and treat - connection of liquor treatment plant to new odour control plant | Process emissions | No | Expenditure to cover assets to capture emissions not requested for 2020-2025 | Yes | Capture of N2O for no other purpose but to prevent emission | Yes |  | Pass | Net Zero primary driver | 17 | ANH | CWW22.17 | Whitlingham STC Fugitive Emissions N2O
| 18 | ANH | CWW22.18 | Cotton Valley WRC Fugitive emissions N2O | Process modification to extend the anoxic zones to increase biodegradation and reduce N2O; and Real Time Control which includes the use of sensors and monitoring equipment including liquid and gas sensors. This monitoring is connected online monitoring and process control, such as adjusting air flow or ammonia-based aeration control (ABAC). The load can also be adjusted. This tends to require some infrastructure changes including adjustable nozzle upgrades for aeration blowers. | Process emissions | No | Expenditure to upgrade assets for N2O not requested for 2020-2025 | Yes | Reduction of N2O emissions the primary driver | Yes |  | Pass | Net Zero primary driver | 18 | ANH | CWW22.18 | Cotton Valley WRC Fugitive emissions N2O
| 19 | ANH | CWW22.19 | Great Billing WRC Fugitive Emissions N2O | Enhanced aeration is a process modification to increase air flow for aerobic biodegradation. Real Time Control includes the use of sensors and monitoring equipment including liquid and gas sensors. This monitoring is connected online monitoring and process control, such as adjusting air flow or ammonia-based aeration control (ABAC). The load can also be adjusted. This tends to require some infrastructure changes including adjustable nozzle upgrades for aeration blowers. | Process emissions | No | Expenditure to upgrade assets for N2O not requested for 2020-2025 | Yes | Reduction of N2O emissions the primary driver | Yes |  | Pass | Net Zero primary driver | 19 | ANH | CWW22.19 | Great Billing WRC Fugitive Emissions N2O
| 20 | ANH | CWW22.20 | Basildon WRC Fugitive Emissions N2O | Anoxic extension is a process modification to extend the anoxic zones to increase biodegradation and reduce N2O. Aeration upgrade is a process modification to increase air flow for aerobic biodegradation. Real Time Control includes the use of sensors and monitoring equipment including liquid and gas sensors. This monitoring is connected online monitoring and process control, such as adjusting air flow or ammonia-based aeration control (ABAC). The load can also be adjusted. This tends to require some infrastructure changes including adjustable nozzle upgrades for aeration blowers. | Process emissions | No | Expenditure to upgrade assets for N2O not requested for 2020-2025 | Yes | Reduction of N2O emissions the primary driver | Yes |  | Pass | Net Zero primary driver | 20 | ANH | CWW22.20 | Basildon WRC Fugitive Emissions N2O
| 21 | ANH | CWW22.21 | Bedford WRC Fugitive Emissions N2O | Diffuser upgrade to modify the aeration supplied to the wastewater load. Real Time Control includes the use of sensors and monitoring equipment including liquid and gas sensors. This monitoring is connected online monitoring and process control, such as adjusting air flow or ammonia-based aeration control (ABAC). The load can also be adjusted. This tends to require some infrastructure changes including adjustable nozzle upgrades for aeration blowers. | Process emissions | No | Expenditure to upgrade assets for N2O not requested for 2020-2025 | Yes | Reduction of N2O emissions the primary driver | Yes |  | Pass | Net Zero primary driver | 21 | ANH | CWW22.21 | Bedford WRC Fugitive Emissions N2O
| 22 | ANH | CWW22.22 | Kings Lynn WRC Fugitive Emissions N2O | Real Time Control includes the use of sensors and monitoring equipment including liquid and gas sensors. This monitoring is connected online monitoring and process control, such as adjusting air flow or ammonia-based aeration control (ABAC). The load can also be adjusted. This tends to require some infrastructure changes including adjustable nozzle upgrades for aeration blowers. | Process emissions | No | Expenditure to upgrade assets for N2O not requested for 2020-2025 | Yes | Reduction of N2O emissions the primary driver | Yes |  | Pass | Net Zero primary driver | 22 | ANH | CWW22.22 | Kings Lynn WRC Fugitive Emissions N2O
| 23 | ANH | CWW22.23 | Newton Marsh WRC Fugitive Emissions N2O | Real Time Control includes the use of sensors and monitoring equipment including liquid and gas sensors. This monitoring is connected online monitoring and process control, such as adjusting air flow or ammonia-based aeration control (ABAC). The load can also be adjusted. This tends to require some infrastructure changes including adjustable nozzle upgrades for aeration blowers. | Process emissions | No | Expenditure to upgrade assets for N2O not requested for 2020-2025 | Yes | Reduction of N2O emissions the primary driver | Yes |  | Pass | Net Zero primary driver | 23 | ANH | CWW22.23 | Newton Marsh WRC Fugitive Emissions N2O
| 24 | ANH | CWW22.24 | Broadholme WRC Fugitive Emissions N2O | Diffuser upgrade to modify the aeration supplied to the wastewater load in the Activated Sludge Process. Real Time Control includes the use of sensors and monitoring equipment including liquid and gas sensors. This monitoring is connected online monitoring and process control, such as adjusting air flow or ammonia-based aeration control (ABAC). The load can also be adjusted. This tends to require some infrastructure changes including adjustable nozzle upgrades for aeration blowers. | Process emissions | No | Expenditure to upgrade assets for N2O not requested for 2020-2025 | Yes | Reduction of N2O emissions the primary driver | Yes |  | Pass | Net Zero primary driver | 24 | ANH | CWW22.24 | Broadholme WRC Fugitive Emissions N2O
| 25 | ANH | CWW22.25 | Letchworth WRC Fugitive emissions N2O | Membrane Aerated Biofilm Reactors impact Net Zero by reducing energy demand of forced aeration treatments but could also be associated with significantly reduced nitrous oxide (N2O) process emissions. The MABR is supported by upgrades to Aeration and RTC. | Process emissions | No | Expenditure to upgrade assets for N2O not requested for 2020-2025 | Yes | Reduction of N2O emissions the primary driver | Yes |  | Pass | Net Zero primary driver. Innovative technology and opportunity for sector learning | 25 | ANH | CWW22.25 | Letchworth WRC Fugitive emissions N2O
| 26 | ANH | CWW22.26 | Newmarket WRC Fugitive Emissions N2O | Membrane Aerated Biofilm Reactors impact Net Zero by reducing energy demand of forced aeration treatments but could also be associated with significantly reduced nitrous oxide (N2O) process emissions. The MABR is supported by upgrades to Aeration and RTC. | Process emissions | No | Expenditure to upgrade assets for N2O not requested for 2020-2025 | Yes | Reduction of N2O emissions the primary driver | Yes |  | Pass | Net Zero primary driver. Innovative technology and opportunity for sector learning | 26 | ANH | CWW22.26 | Newmarket WRC Fugitive Emissions N2O
| 27 | ANH | CWW22.27 | Hitchin WRC Fugitive emissions N2O | Anoxic extension is a process modification to extend the anoxic zones to increase biodegradation and reduce N2O. Real Time Control includes the use of sensors and monitoring equipment including liquid and gas sensors. This monitoring is connected to online monitoring and process control, such as adjusting air flow or ammonia-based aeration control (ABAC). The load can also be adjusted. This tends to require some infrastructure changes including adjustable nozzle upgrades for aeration blowers. | Process emissions | No | Expenditure to upgrade assets for N2O not requested for 2020-2025 | Yes | Reduction of N2O emissions the primary driver | Yes |  | Pass | Net Zero primary driver | 27 | ANH | CWW22.27 | Hitchin WRC Fugitive emissions N2O
| 28 | ANH | CWW22.28 | Dunstable WRC Fugitive Emissions N2O | Membrane Aerated Biofilm Reactors impact Net Zero by reducing energy demand of forced aeration treatments but could also be associated with significantly reduced nitrous oxide (N2O) process emissions. The MABR is supported by upgrades to Aeration and RTC. | Process emissions | No | Expenditure to upgrade assets for N2O not requested for 2020-2025 | Yes | Reduction of N2O emissions the primary driver | Yes |  | Pass | Net Zero primary driver. Innovative technology and opportunity for sector learning | 28 | ANH | CWW22.28 | Dunstable WRC Fugitive Emissions N2O
| 29 | ANH | CWW22.29 | Flitwick WRC Fugitive Emissions N2O | Membrane Aerated Biofilm Reactors impact Net Zero by reducing energy demand of forced aeration treatments but could also be associated with significantly reduced nitrous oxide (N2O) process emissions. The MABR is supported by upgrades to Aeration and RTC. | Process emissions | No | Expenditure to upgrade assets for N2O not requested for 2020-2025 | Yes | Reduction of N2O emissions the primary driver | Yes |  | Pass | Net Zero primary driver. Innovative technology and opportunity for sector learning | 29 | ANH | CWW22.29 | Flitwick WRC Fugitive Emissions N2O
| 30 | ANH | CWW22.30 | Great Billing STC Liquor Ammonia | Centrate treatment plant - construction of a liquor treatment plant - New sludge liquor treatment plant established at our largest sludge treatment centre, designed and operated to minimise nitrous oxide emissions from outset, including covering and treating nitrous oxide in off-gas. Currently the centrate is returned to the existing wastewater treatment works. | Process emissions | No | This is process is to capture and mitigate N2O from liquor treatment | Yes | Delivery of a new site. Net Zero incorporated into delivery planning. | No |  | Fail | Scheme proposes to construct a new liquor treatment plant, this is Base expenditure. | 30
| 31 | ANH | CWW22.31 | Logistics Fleet CO2 emissions 2025-26 | Electrification of HGVs 2025-26 | Transport | Yes | Transport historically funded under base expenditure. | Yes | Clear net zero driver - HGVs represent 70% of transport emissions | No |  | Fail | Should continue to be funded by Base expenditure | 31
| 32 | ANH | CWW22.32 | Logistics fleet CO2 emissions 2026-27 | Electrification of HGVs | Transport | Yes | Transport historically funded under base expenditure. | Yes | Clear net zero driver - HGVs represent 70% of transport emissions | No |  | Fail | Should continue to be funded by Base expenditure | 32
| 33 | ANH | CWW22.33 | Logistics fleet CO2 emissions 2027-28 | Electrification of HGVs | Transport | Yes | Transport historically funded under base expenditure. | Yes | Clear net zero driver - HGVs represent 70% of transport emissions | No |  | Fail | Should continue to be funded by Base expenditure | 33
| 34 | ANH | CWW22.34 | Logistics fleet CO2 emissions 2028-29 | Electrification of HGVs | Transport | Yes | Transport historically funded under base expenditure. | Yes | Clear net zero driver - HGVs represent 70% of transport emissions | No |  | Fail | Should continue to be funded by Base expenditure | 34
| 35 | ANH | CWW22.35 | Logistics fleet CO2 emissions 2029-30 | Electrification of HGVs | Transport | Yes | Transport historically funded under base expenditure. | Yes | Clear net zero driver - HGVs represent 70% of transport emissions | No |  | Fail | Should continue to be funded by Base expenditure | 35
| 36 | ANH | CWW22.36 | Huntingdon WRC Fugitive Emissions N2O | Enhanced aeration is a process modification to increase air flow for aerobic biodegradation. Real Time Control includes the use of sensors and monitoring equipment including liquid and gas sensors. This monitoring is connected online monitoring and process control, such as adjusting air flow or ammonia-based aeration control (ABAC). The load can also be adjusted. This tends to require some infrastructure changes including adjustable nozzle upgrades for aeration blowers. | Process emissions | No | Expenditure to upgrade assets for N2O not requested for 2020-2025 | Yes | Reduction of N2O emissions the primary driver | Yes |  | Pass | Net Zero primary driver | 36 | ANH | CWW22.36 | Huntingdon WRC Fugitive Emissions N2O
| 37 | ANH | CWW22.37 | AMP8 Small Scale Solar Delivery WR | WR Mounted Panels | Renewable energy | No | Renewables excluded from price review | Yes | Clear net zero driver | No | In our 2008 letter to the sector, we stated that our starting presumption is that companies’ renewable activities should not form part of the appointed business (i.e. a company's functions) unless there are compelling reasons for this. A 2021 board paper further outlined this position with renewables considered non-appointed business with rules in place (e.g. on transfer prices) to protect customers and mitigate the risks of cross-subsidy. | Fail | Not a core business activity | 37
| 38 | ANH | CWW22.38 | Basildon STC Gas to Grid | Biogas Upgrading & Injection to Grid Rev 2 | Gas to grid | Yes | Gas to grid delivered under base expenditure for 2020-2025. | Yes | Carbon benefit but also revenue generating scheme | No |  | Fail | Should continue to be funded by Base expenditure | 38
| 39 | ANH | CWW22.39 | Colchester STC Gas to Grid | Biogas Upgrading & Injection to Grid Rev 2 | Gas to grid | Yes | Gas to grid delivered under base expenditure for 2020-2025. | Yes | Carbon benefit but also revenue generating scheme | No |  | Fail | Should continue to be funded by Base expenditure | 39
| 40 | ANH | CWW22.40 | Ipswich Cliff Quay STC Gas to Grid | Biogas Upgrading & Injection to Grid Rev 2 | Gas to grid | Yes | Gas to grid delivered under base expenditure for 2020-2025. | Yes | Carbon benefit but also revenue generating scheme | No |  | Fail | Should continue to be funded by Base expenditure | 40
| 41 | ANH | CWW22.41 | Pyewipe STC Gas to Grid | Biogas Upgrading & Injection to Grid Rev 2 | Gas to grid | Yes | Gas to grid delivered under base expenditure for 2020-2025. | Yes | Carbon benefit but also revenue generating scheme | No |  | Fail | Should continue to be funded by Base expenditure | 41
| 42 | ANH | CWW22.42 | Kings Lynn STC gas to grid | Biogas Upgrading & Injection to Grid Rev 2 | Gas to grid | Yes | Gas to grid delivered under base expenditure for 2020-2025. | Yes | Carbon benefit but also revenue generating scheme | No |  | Fail | Should continue to be funded by Base expenditure | 42
| 43 | ANH | CWW22.43 | Whitlingham WRC Fugitive Emissions N2O | Real Time Control includes the use of sensors and monitoring equipment including liquid and gas sensors. This monitoring is connected online monitoring and process control, such as adjusting air flow or ammonia-based aeration control (ABAC). The load can also be adjusted. This tends to require some infrastructure changes including adjustable nozzle upgrades for aeration blowers. | Process emissions | No | Expenditure to upgrade assets for N2O not requested for 2020-2025 | Yes | Intervention for reduction in N2O. Possible driver for efficiency and better operation of assets. | No |  | Fail | Net Zero primary driver. Potential driver of improved asset operation and performance | 43
| 44 | ANH | CWW22.44 | Colchester WRC Fugitive Emissions N2O | Real Time Control includes the use of sensors and monitoring equipment including liquid and gas sensors. This monitoring is connected online monitoring and process control, such as adjusting air flow or ammonia-based aeration control (ABAC). The load can also be adjusted. This tends to require some infrastructure changes including adjustable nozzle upgrades for aeration blowers. | Process emissions | No | Expenditure to upgrade assets for N2O not requested for 2020-2025 | Yes | Intervention for reduction in N2O. Possible driver for efficiency and better operation of assets. | No |  | Fail | Net Zero primary driver. Potential driver of improved asset operation and performance | 44
| 45 | ANH | CWW22.45 | Colchester WRC Fugitive Emissions N2O | Membrane Aerated Biofilm Reactor is a technology which combines high nutrient removal and energy efficiency compared to traditional systems. It enables simultaneous nitrification-denitrification in a single tank and produce a high-quality effluent. They can reduce aeration energy use significantly. The MABR is supported by upgrades to Aeration and RTC. | Process emissions | No | Expenditure to upgrade assets for N2O not requested for 2020-2025 | Yes | Capture of N2O for no other purpose but to prevent emission | Yes |  | Pass | Net Zero primary driver. Innovative technology and opportunity for sector learning | 45 | ANH | CWW22.45 | Colchester WRC Fugitive Emissions N2O
| 46 | HDD | CWW22.1 | Process Emissions Reduction | (HDD clarification) A digital twin is a virtual replica of a physical system, process, or product that can be used to simulate, predict, and optimise its performance. In the context of wastewater treatment works, a digital twin will be used to create a detailed model of the entire treatment process, from the inflow of wastewater to the discharge of treated water using a combination of mechanistic models and machine learning. This model can be used to simulate the behaviour of the system under different conditions, optimise the performance of the treatment process, and predict the impact of changes to the system. We intend to use the digital twin system to both reduce the creation and release of harmful greenhouse gases. ASP Cover & Treat to reduce N2O production - Welshpool site | Process emissions | No | Expenditure to upgrade assets for N2O not requested for 2020-2025 | Yes | Capture of N2O for no other purpose but to prevent emission | Yes |  | Pass | Net Zero primary driver | 46 | HDD | CWW22.1 | Process Emissions Reduction
| 47 | HDD | CWW22.2 | Heat Decarbonisation | Replacement of fossil fuel boilers with heat pumps for space heating | Heat pumps | Yes | Heating historically funded under base expenditure. | Yes | National Environment Programme (NEP) driver for net zero | No |  | Fail | Should continue to be funded by Base expenditure | 47
| 48 | SVE | NZ#1 | Digital Twin | Digital Twin uses artificial intelligence, machine learning and mechanistic models to optimise the processes. Digital Twin has been identified for larger, more complex and dynamic processes. (SVE) [Digital Twin] can be described as real-time control, but we believe it represents the pinnacle of what is technically achievable and that all real-time control systems cannot considered to be equivalent. | Process emissions | No | New technology not requested for funding for 2020-2025 | Yes | Novel technology to support reduction in N2O emissions | Yes |  | Pass | Net Zero primary driver. Innovative technology and opportunity for sector learning | 48 | SVE | NZ#1 | Digital Twin
| 49 | SVE | NZ#2 | Cover & Treat | Containment, or cover and treatment, of emissions involves building an impermeable canopy over wastewater treatment works to capture N2O emitted by activated sludge plants. The N2O is treated using a photocatalytic membrane which breaks down the gas into N2 and O2. | Process emissions | No | Expenditure to cover assets to capture emissions not requested for 2020-2025 | Yes | Capture of N2O for no other purpose but to prevent emission | Yes |  | Pass | Net Zero primary driver | 49 | SVE | NZ#2 | Cover & Treat
| 50 | SVE | NZ#3 | ASP Intensification | Membrane Aerated Biofilm Reactor is a technology which combines high nutrient removal and energy efficiency compared to traditional systems. It enables simultaneous nitrification-denitrification in a single tank and produce a high-quality effluent. They can reduce aeration energy use significantly. The MABR is supported by upgrades to Aeration and RTC. | Process emissions | No | Expenditure to upgrade assets for N2O not requested for 2020-2025 | Yes | Novel technology to support reduction in N2O emissions | Yes |  | Pass | Net Zero primary driver. Innovative technology and opportunity for sector learning | 50 | SVE | NZ#3 | ASP Intensification
| 51 | SVE | NZ#4 | Active gas capture | More effective digestion and removal of CH4 in the digester vessels, resulting in less carryover into downstream tanks. Digestate is then passed through a vacuum degassing process to remove any remaining traces of methane | Process emissions | No | Expenditure to upgrade assets for N2O not requested for 2020-2025 | Yes | Methane capture in the bioresources stage of wastwater treatment is the primary driver. This is driven by Net Zero, it is outside of the requirements set by the Industrial Emissions Directive. | Yes |  | Pass | Driver is methane capture. | 51 | SVE | NZ#4 | Active gas capture
| 52 | SVE | NZ#5 | EV Charging Infrastructure | EV charge points | Transport | Yes | Transport historically funded under base expenditure. | Yes | Scheme continues investment in EV charging infrastructure for 2020-2025 (350 units already installed) | Yes |  | Fail | Should continue to be funded by Base expenditure | 52
| 53 | SVE | NZ#6 | Heat pumps | Replacement of fossil fuel boilers with heat pumps for space heating | Heat pumps | Yes | Heating historically funded under base expenditure. | Yes | A technological upgrade which is purely for the benefit of reducing direct consumption of fossil fuels for space heating | Yes |  | Fail | Should continue to be funded by Base expenditure | 53
| 54 | SVE | NZ#7 | HVO diesel replacement | Infrastructure to enable replacement of mineral diesel with HVO | Transport | Yes | Transport historically funded under base expenditure. | Yes | Transition to HVO to reduce dependence on fossil diesel | Yes |  | Fail | Should continue to be funded by Base expenditure | 54
| 55 | SVE | NZ#8 | Cellulose recovery | Cellulose recovery to use it to heat the biomass boilers, typically thermal hydrolysis sludge treatment. | Fossil fuel reduction | No | Boiler upgrade Should continue to be funded by Base expenditure. | Yes | Reduction in fossil fuel use | Yes |  | Pass | Should continue to be funded by Base expenditure | 55 | SVE | NZ#8 | Cellulose recovery
| 56 | SVE | NZ#9 | Process Optimisation | Instrumentation & optimisation to reduce N2O production. Real Time Control includes the use of sensors and monitoring equipment including liquid and gas sensors. This monitoring is connected online monitoring and process control, such as adjusting air flow or ammonia-based aeration control (ABAC). The load can also be adjusted. This tends to require some infrastructure changes including adjustable nozzle upgrades for aeration blowers. | Process emissions | No | Expenditure to upgrade assets for N2O not requested for 2020-2025 | Yes | Capture of N2O for no other purpose but to prevent emission | Yes |  | Pass | Net Zero primary driver. | 56 | SVE | NZ#9 | Process Optimisation
| 57 | SVE | NZ#10 | Hydrogen Production | Production of hydrogen by electrolysis of high strength liquors | Energy | Yes | Energy scheme historically funded under base expenditure. SVE also considers it to be base expenditure. | Yes | Support switch from fossil fuel energy | Yes |  | Fail | Should continue to be funded by Base expenditure. Severn Trent Water accepted this is Base expenditure in its submission. | 57
| 58 | SVE | NZ#11 | Electrical storage | Behind the meter battery storage | Energy | Yes | Energy scheme historically funded under base expenditure. SVE also considers it to be base expenditure. | Yes | Behind the metter battery storage to increase resilience of electricity supply | Yes |  | Fail | Should continue to be funded by Base expenditure. Severn Trent Water accepted this is Base expenditure in its submission. | 58
| 59 | SVE | NZ#12 | EV fleet only | EV vehicles | Transport | Yes | Transport historically funded under base expenditure. SVE also considers it is a base activity. | Yes | Decarbonisation of the vehicle fleet | Yes |  | Fail | Should continue to be funded by Base expenditure. Severn Trent Water accepted this is Base expenditure in its submission. | 59
| 60 | SVE | NZ#13 | HVO fuel only | HVO (marginal cost of fuel only) | Transport | Yes | Transport historically funded under base expenditure. SVE also considers it is a base activity. | Yes | Bunkers to support transition to HVO to reduce dependence on fossil diesel | Yes |  | Fail | Should continue to be funded by Base expenditure. Severn Trent Water accepted this is Base expenditure in its submission. | 60
| 61 | SVE | NZ#14 | Solar PV | Solar PV (other than very small scale) | Renewable energy | No | Renewables excluded from price review | Yes | Procurement of renewables infrastructure to reduce energy demand and provide clean electricity | yes | In our 2008 letter to the sector, we stated that our starting presumption is that companies’ renewable activities should not form part of the appointed business (i.e. a company's functions) unless there are compelling reasons for this. A 2021 board paper further outlined this position with renewables considered non-appointed business with rules in place (e.g. on transfer prices) to protect customers and mitigate the risks of cross-subsidy. | Fail | Not a core business activity | 61
| 62 | TMS | CWW22_1 | S40749/1 (Long Reach - Installation of Biomethane Plant - Delta from botex for bidding process) | Switch from CHP powered by biogas to conversion of biogas to biomethane, with injection to grid. CHP engines are life expired in 2025-2030; base costs of CHP replacement have been removed. | Gas to grid | Yes | Gas to grid delivered under base expenditure for 2020-2025. | Yes | Carbon benefit but also revenue generating scheme | Yes |  | Fail | Should continue to be funded by Base expenditure | 62
| 63 | TMS | CWW22_2 | Aylesbury - Installation of Biomethane Plant with heat pump - Delta from botex for bidding process | Switch from CHP powered by biogas to conversion of biogas to biomethane, with injection to grid. CHP engines are life expired in 2025-2030; base costs of CHP replacement have been removed. | Gas to grid | Yes | Gas to grid delivered under base expenditure for 2020-2025. | Yes | Carbon benefit but also revenue generating scheme | Yes |  | Fail | Should continue to be funded by Base expenditure | 63
| 64 | TMS | CWW22_3 | Bishop Stortford - Installation of Biomethane Plant - enhancement from botex for bidding process | Switch from CHP powered by biogas to conversion of biogas to biomethane, with injection to grid. CHP engines are life expired in 2025-2030; base costs of CHP replacement have been removed. | Gas to grid | Yes | Gas to grid delivered under base expenditure for 2020-2025. | Yes | Carbon benefit but also revenue generating scheme | Yes |  | Fail | Should continue to be funded by Base expenditure | 64
| 65 | TMS | CWW22_4 | Didcot - Installation of Biomethane Plant - enhancement from botex for bidding process | Switch from CHP powered by biogas to conversion of biogas to biomethane, with injection to grid. CHP engines are life expired in 2025-2030; base costs of CHP replacement have been removed. | Gas to grid | Yes | Gas to grid delivered under base expenditure for 2020-2025. | Yes | Carbon benefit but also revenue generating scheme | Yes |  | Fail | Should continue to be funded by Base expenditure | 65
| 66 | TMS | CWW22_5 | East Hyde - Installation of Biomethane Plant - enhancement from botex for bidding process | Switch from CHP powered by biogas to conversion of biogas to biomethane, with injection to grid. CHP engines are life expired in 2025-2030; base costs of CHP replacement have been removed. | Gas to grid | Yes | Gas to grid delivered under base expenditure for 2020-2025. | Yes | Carbon benefit but also revenue generating scheme | Yes |  | Fail | Should continue to be funded by Base expenditure | 66
| 67 | TMS | CWW22_6 | Hogsmill -Installation of Biomethane Plant - enhancement from botex for bidding process | Switch from CHP powered by biogas to conversion of biogas to biomethane, with injection to grid. CHP engines are life expired in 2025-2030; base costs of CHP replacement have been removed. | Gas to grid | Yes | Gas to grid delivered under base expenditure for 2020-2025. | Yes | Carbon benefit but also revenue generating scheme | Yes |  | Fail | Should continue to be funded by Base expenditure | 67
| 68 | TMS | CWW22_7 | Reading - Installation of Biomethane Plant - enhancement from botex for bidding process | Switch from CHP powered by biogas to conversion of biogas to biomethane, with injection to grid. CHP engines are life expired in 2025-2030; base costs of CHP replacement have been removed. | Gas to grid | Yes | Gas to grid delivered under base expenditure for 2020-2025. | Yes | Carbon benefit but also revenue generating scheme | Yes |  | Fail | Should continue to be funded by Base expenditure | 68
| 69 | TMS | CWW22_8 | S40040/4 (PR24 Fleet - Life expired Enhancement (cost to convert to electrical) (Waste)) | Linked to water scheme. replacing life expired vehicles- state that embedded emissions component relates to charging infra- unclear if ask includes charging infra and how much of cost relates to this. | Transport | Yes | Transport historically funded under base expenditure. | Yes | Conversion of fleet to EV at end of useful life. | Yes |  | Fail | Should continue to be funded by Base expenditure | 69
| 70 | TMS | CWW22_9 | S40841/1 (PR24 Hybrid air source heat pump/existing boiler for 4 corporate offices (Waste)) | Additional cost for upgrading from end of life gas boilers to hybrid source, but hybrid will be cheaper to run. | Heat pumps | Yes | Heating historically funded under base expenditure. | Yes | Reduction of emissions through transition to low carbon heat | Yes |  | Fail | Should continue to be funded by Base expenditure | 70
| 71 | TMS | CWW22_10 | S40842/2 (PR24 Air source heat pump for site office (enhancement cost) (Waste)) | Additional cost for upgrading from end of life gas boilers to heat pumps, but heat pumps will be cheaper to run. | Heat pumps | Yes | Heating historically funded under base expenditure. | Yes | Reduction of emissions through transition to low carbon heat | Yes |  | Fail | Should continue to be funded by Base expenditure | 71
| 72 | NWT | E00001337 | Stationary fossil fuel reductions | New equipment at sludge treatment centres to transition from fossil fuels to a renewable alternative in the sludge or wastewater treatment processes (e.g. biogas, hydrogen, HVO, or heat pumps and electric boilers). | Fossil fuel reduction | Yes | Boiler upgrade Should continue to be funded by Base expenditure (extension of gas to grid decision). | Yes | The scheme is clearly driven by net zero, contributing to reducing fossil fuel. The business case is well-evidenced apart from missing information on how it would contribute to sector learning. It would include locally produced biogas, hydrogen, or other fuels such as HVO or through technologies such as heat pumps and electric boilers | No |  | Fail | Should continue to be funded by Base expenditure | 72
| 73 | NWT | E00001338 | Process emissions (Bioresources) | This net zero enhancement provides a major reduction in fugitive methane releases. The proposal is to use new technology to extract more biogas from the sludge which would have otherwise be lost to atmosphere. This refers to Vaccum Degassing: Upgrade to the digester to include vacuum degassing and leak detection. This is described by UU as a “novel” solution, it is a pump attached to a tank which withdraws gas from the sewage sludge reducing the residual emissions in the sludge and increasing its density. | Process emissions | No | Maintenance of assets under base. Spend to save (commercial opportunity from methane collection) not provided for in base. | Yes | Carbon benefit but also revenue generating scheme | No |  | Fail | Should continue to be funded by Base expenditure | 73
| 74 | NWT | E00001339 | Process emissions (Wastewater) | (UUW) Introduce innovative technologies to monitor and reduce the release of nitrous oxide from wastewater processes. Sector leading nitrous oxide (N2O) emissions reduction programme. (Interpretation from narrative is this is Real Time Control). Real Time Control includes the use of sensors and monitoring equipment including liquid and gas sensors. This monitoring is connected online monitoring and process control, such as adjusting air flow or ammonia-based aeration control (ABAC). The load can also be adjusted. This tends to require some infrastructure changes including adjustable nozzle upgrades for aeration blowers. | Process emissions | No | Expenditure to upgrade assets for N2O not requested for 2020-2025 | Yes | Capture of N2O for no other purpose but to prevent emission | Yes |  | Pass | Net Zero primary driver. | 74 | NWT | E00001339 | Process emissions (Wastewater)
| 75 | NWT | E00001340 | Transport fossil fuel reductions - Green fleet LCVs phase 1 | Procuring zero emission (Electric Vehicle, EV) cars & vans | Transport | Yes | Transport historically funded under base expenditure. The scheme replaces light commercial vehicles (diesel) at their end of their life cycle, and the enhancement case is only the extra costs from the base allowance for 2025-2030. They should be doing it from their base allowance. | Yes | Replacing vehicles at their end of life | Yes |  | Fail | Should continue to be funded by Base expenditure | 75
| 76 | NWT | E00001341 | Transport fossil fuel reductions - Green fleet LCVs phase 2 | Procuring zero emission (Electric Vehicle, EV) cars & vans | Transport | Yes | Transport historically funded under base expenditure. The scheme includes the cost for switching away from fossil fuel vehicles, complementing 2025-2030 base allowances to replace some vehicles with a like for like option. But it concerns light commercial vehicles and will replace them before their end of life to make sure the all fleet is converted before the end of 2025-2030. | Yes | Switch of vehicles to EVs before their end of life | No |  | Fail | Should continue to be funded by Base expenditure | 76
| 77 | NWT | E00001342 | Transport fossil fuel reductions - Green fleet Biomethane HGVs | Switching to biofuel for Bioresources HGV's. | Transport | Yes | Transport historically funded under base expenditure. | Yes | Switch of HGVs to EVs will significantly reduce transport emissions | Yes |  | Fail | Should continue to be funded by Base expenditure | 77
| 78 | NWT | E00001426 | Phase 2 – Further low regrets emissions reductions in AMP8 | A selection of projects with GHG emissions as the primary driver for consideration within 2025-2030. Due to the uncertainty and rapid evolution within the market the potential cases within our proposed phase 2 require further investigation and will be defined within 2025-2030. The scheme is to secure funding to continue exploring the deployment of technologies proposed in schemes E00001338 and E00001339. | Process emissions | Yes | Interventions mentioned include base expenditure (transport) and enhancement (P-removal). | Yes | The company states this project would focus on a second phase of the process emission projects in wastewater and/or bioresources, taking learning from the first phase to develop our understanding further. | No |  | Fail | The intervention is to continue exploring the deployment of interventions proposed under E00001338 and E00001339. This is dependent on the outcome of those schemes and therefore poses uncertainty. | 78
| 79 | NWT | E00001346 | Property emissions reductions | Decarbonising heat within our UUW owned property portfolio, focused at moving away from fossil fuel usage. | Heat pumps | Yes | Heating historically funded under base expenditure. | Yes | The scheme is enhancement (replacement of boilers and setting up a low emission heating system), with net zero being the driver. This is not maintenance as the project involves replacing functioning assets | No |  | Fail | Should continue to be funded by Base expenditure | 79
| 80 | NWT | E00001425 | Net zero catchment strategy | Working with partners, UU wants to develop a sustainability masterplan and test innovative approaches ​for low carbon water and wastewater priorities in the major new development of St Cuthbert's Garden ​Village (10,000 houses over a 30y period). This could include working with developers on storing surface water, recycling grey water, exploring ways to protect the sewers in operation (such as making smarter design choices and increasing community engagement) and potential reuse of low-grade heat from the sewer network. Also include minimising the need at the treatment works (enhanced treatment solutions and local composting) and opportunities to re-use by products from the treatment process. Carbon benefits are uncertain since UU still has to decide on specific interventions. ​ | NBS | No | Clear enhancement scheme | Yes | Development of a net zero catchment strategy | Yes |  | Pass | Net Zero primary driver. | 80 | NWT | E00001425 | Net zero catchment strategy
| 81 | WSH | CWW22_1 | Net Zero Carbon Strategy: Network Control Systems (Wastewater) | Delivery of a new Network Control System for Wastewater to reduce energy consumption by using factors such as weather and demand patterns to predict optimum set points, and as a result, control and optimise pumping regimes | Process emissions | Yes | This is to operate assets efficiently and effectively and comes under base expenditure | Yes | The scheme will deliver efficiencies in the operation of the asset which are not certain to deliver emissions reductions or reduction in energy consumption | Yes |  | Pass | Should continue to be funded by Base expenditure | 81 | WSH | CWW22_1 | Net Zero Carbon Strategy: Network Control Systems (Wastewater)
| 82 | WSH | CWW22_2 | Net Zero Carbon Strategy: Reduction of Process Emissions | This enhanced investment case will deliver an advanced process control system to reduce N2O emissions and reduce energy consumption (enabled by investment in new blowers at 14 sites and new diffusers at 20 sites). Real Time Control - Use of sensors and monitoring equipment including liquid and gas sensors. This monitoring is connected online monitoring and process control, such as adjusting air flow or ammonia-based aeration control (ABAC). The load can also be adjusted. This tends to require some infrastructure changes such as new blowers and diffusers. | Process emissions | Yes | This is to operate assets efficiently and effectively and comes under base expenditure | Yes | The scheme will deliver efficiencies in the operation of the asset which are not certain to deliver emissions reductions or reduction in energy consumption | Yes |  | Pass | Net Zero Primary Driver | 82 | WSH | CWW22_2 | Net Zero Carbon Strategy: Reduction of Process Emissions
| 83 | WSX | CWW22_1 | Heat recovery | Heat recovery (Avo SBR effluent) - displacing fossil gas | Fossil fuel reduction | No | Heating historically funded under base expenditure. | Yes | Seeks to offset use of gas through use of a heatpump and injection of biomethane to grid | Yes |  | Pass | Should be funded by Base Uplift | 83 | WSX | CWW22_1 | Heat recovery
| 84 | WSX | CWW22_2 | Nitrous oxide - standard enhancement | Monitoring & control of N2O at 7 sites (out of total 20), under standard enhancement drivers. Use of sensors and monitoring equipment including liquid and gas sensors. This monitoring is connected online monitoring and process control, such as adjusting air flow or ammonia-based aeration control (ABAC). The load can also be adjusted. Controlling emissions tends to require some infrastructure changes such as adjustable blowers and diffusers. | Process emissions | No | This is to operate assets efficiently and effectively and comes under base expenditure | Yes | Seven sites where enhancement investment is planned for 2025-2030 where the driver is another service improvement e.g. improved water quality in rivers of estuaries. The nitrous oxide monitoring in these cases will be classed as standard enhancement. | Yes |  | Pass | The primary driver for these 7 site interventions is by another enhancement driver | 84 | WSX | CWW22_2 | Nitrous oxide - standard enhancement
| 85 | WSX | CWW22_3 | Nitrous oxide - NZ challenge | Monitoring & control, 13 sites (out of 20), net zero carbon challenge. Investigatory monitoring will take place for two years, with the default technology being sensors that measure N2O in solution in the aqueous phase. Two years of continuous monitoring will help us better understand the cause effect relationships at specific sites of the variables noted above and N2O formation, while also allowing us to see the degree to which N2O spikes can be prevented and whether levels observed at other times can be reduced. After two years of monitoring at the first tranche of sites, rigs will be de-mounted, moved and re-assembled at other WRCs to repeat the exercise. | Process emissions | No | No emissions monitoring was funded under PR19 | Yes | Thirteen sites where there is no other enhancement requirement, which means that net zero carbon is the primary driver. | Yes |  | Pass | The primary driver for these 13 site interventions is net zero | 85 | WSX | CWW22_3 | Nitrous oxide - NZ challenge
| 86 | WSX | CWW22_4 | Transport | Decarbonised fleet infrastructure | Transport | Yes | Transport historically funded under base expenditure. | Yes | Provision of infrastructure to support low emission fleet | Yes |  | Fail | Should continue to be funded by Base expenditure | 86
| 87 | WSX | CWW22_5 | On-site renewables | 1x 3MW wind turbine on WW land | Renewable energy | No | Renewables excluded from price review | Yes | Procurement of renewables infrastructure to reduce energy demand and provide clean electricity | No | In our 2008 letter to the sector, we stated that our starting presumption is that companies’ renewable activities should not form part of the appointed business (i.e. a company's functions) unless there are compelling reasons for this. A 2021 board paper further outlined this position with renewables considered non-appointed business with rules in place (e.g. on transfer prices) to protect customers and mitigate the risks of cross-subsidy. | Fail | Not a core business activity | 87
| 88 | WSX | CWW22_6 | Exported heat | Heat recovery - large pumping station | Heat pumps | Yes | Energy scheme historically funded under base expenditure. WSX also considers it is not deliverable in 2025-2030. | Yes | Procurement of renewables infrastructure to reduce energy demand and provide clean electricity | yes |  | Fail | There was not sufficient information provided on this scheme due to the company judging it non-deliverable. | 88
| 89 | YKY | CWW22-1 | Solar | Combination of rooftop and groundmount solar on YW sites. | Renewable energy | No | Renewables excluded from price review | Yes | Clear net zero driver for investment in renewable energy | yes | In our 2008 letter to the sector, we stated that our starting presumption is that companies’ renewable activities should not form part of the appointed business (i.e. a company's functions) unless there are compelling reasons for this. A 2021 board paper further outlined this position with renewables considered non-appointed business with rules in place (e.g. on transfer prices) to protect customers and mitigate the risks of cross-subsidy. | Fail | Not a core business activity | 89
| 90 | YKY | CWW22-2 | Methane reduction | Investment to reduce methane emissions from process via digester upgrade, vacuum degassing and leak detection | Process emissions | No | Maintenance of assets under base. Spend to save (commercial opportunity from methane collection) not provided for in base. | Yes | Methane capture in the bioresources stage of wastwater treatment is the primary driver. This is driven by Net Zero but could also be driven by IED | Yes |  | Pass | Driver is methane capture. | 90 | YKY | CWW22-2 | Methane reduction
| 91 | YKY | CWW22-3 | Nitrous oxide reduction | Use of sensors and monitoring equipment including liquid and gas sensors. This monitoring is connected online monitoring and process control, such as adjusting air flow or ammonia-based aeration control (ABAC). The load can also be adjusted. This tends to require some infrastructure changes. Investment to reduce nitrous oxide emissions from ASP lanes via use of real time control coupled with monitoring of emission and limited additional investment in liquor buffering. | Process emissions | No | This is to operate assets efficiently and effectively and comes under base expenditure | Yes | Capture of N2O for no other purpose but to prevent emission | Yes |  | Pass | Net Zero primary driver. | 91 | YKY | CWW22-3 | Nitrous oxide reduction
[17 empty] | Totex (£m) | 528.57
|  |  | Totex (£m) | 625.9407 | [12 empty] | AMP8 benefits (tCO2e) | -335861.971
|  |  | AMP8 benefits (tCO2e) | -428498.463
Process description This phase sought to establish whether the scheme is eligible for Net Zero Enhancement funding. In our process we reviewed each scheme narrative, associated costs, and projected emissions reductions forecast in the Business Plan Table (Table CWW22). Scheme details were assessed to ascertain whether: - those technologies should or could be funded by Base; - had been funded in a previous Price Review; - determine if Net Zero is the primary driver. Further to these questions, scheme details were assessed for: - alignment with company net zero goals and Long Term Delivery Strategy - alignment with Ofwat's Net Zero Principles Overview of decisions Schemes passed to the next phase showed clearly that: - Net Zero is the primary driver, even if there were other commercial drivers or otherwise associated with the scheme - the scheme was not previously funded under Base expenditure at a previous Price Review - the scheme is a core business activity - the scheme was not driven by obligations set by WINEP or the Industrial Emissions Directive

## Phase 2 - Net Zero Value
#VALUE!
Is the scheme supporting UK government net zero targets, innovation and sector learning and align with our net zero principles
| Scheme submitted |  |  |  | Scheme description |  | Additional information requested |  |  | Assessment of tech maturity and contribution to innovation, learning and efficiency. (Innovation judgements were supported by the Ofwat Net Zero Technology Review https://www.ofwat.gov.uk/publication/net-zero-technology-review/ Technology Readiness Levels have been provided where available[https://www.ukri.org/councils/stfc/guidance-for-applicants/check-if-youre-eligible-for-funding/eligibility-of-technology-readiness-levels-trl/]) |  | Confidence of impact on emissions |  | IED overlap |  | Decisions of phase 2 |  | Results of phase 2
|  | Company | Scheme ID | Scheme name | Category | Scheme description | Query link | Purpose of query | Response/Description of technology | Innovation level | Justification | Confidence level | Justification | Overlap (Yes/No) | Justification | Phase 2 assessment decision (pass/fail) | Justification |  | Company | Scheme ID | Scheme name | AMP8 totex (£m, 2025-30)
| 1 | ANH | CWW22.1 | Cotton Valley STC - Centrate quality | Process emissions | Liquor recovery - Installation of Ammonia stripping and recovery into liquid Ammonium Sulphate. The cost includes the up and downstream pumping of flows to the recovery plant, product storage and loading facilities. | Environment team - OFW-OBQ-ANH-163.pdf - All Documents (sharepoint.com) | To understand further detail of the scheme and to support determination if it is affected by the IED | Liquor recovery - Installation of Ammonia stripping and recovery into liquid Ammonium Sulphate. The cost includes the up and downstream pumping of flows to the recovery plant, product storage and loading facilities. | TRL 7 - technology prototype demonstration in an operational environment | Ammonia stripping provides an N2O mitigation pathway, however there are concerns that the steam requirement might offset carbon emissions saved as a reliable source of steam is essential to the process. As an innovation and learning exercise this poses an opportunity for N2O reduction. | Low | Ofwat Technology Review suggests reductions in N2O might be offset by increases in CO2 in the provision of steam. Careful carbon assessments are advised in the technology summary. | No | Scheme is applicable to liquors from the bio-reactor, primary and secondary settlement tanks. | Pass | This scheme reduces GHG emissions in the early stages of the wastewater treatment process. There are concerns regarding the viability of the project in terms of net GHG emissions, however due to the innovative nature of the scheme and opportunity for sector learning this scheme has been passed. | 1 | ANH | CWW22.1 | Cotton Valley STC - Centrate quality | 14.567
| 2 | [14 empty] | Fail |  | 2 |  |  |  | 9.309
| 3 | [14 empty] | Fail |  | 3 |  |  |  | 7.023
| 4 | [5 empty] | Environment team - OFW-OBQ-ANH-163.pdf - All Documents (sharepoint.com) | Request direction for finding further details of the sites and their specific interventions under each scheme | Covering of open digester limpet chambers to entrain gas Vacuum degassing of the digestate and connection to the gas header. Covering of the post digestion storage tank, with appropriate safety systems to prevent over pressurisation of these tanks and connection to the gas header. Replacement of the post digestion aeration system with gas mixing and the installation of a final stage of flash aeration (covered and odour controlled) prior to dewatering | Methane containment - mature Vacuum Degassing - TRL 7 - technology prototype demonstration in an operational environment Covering of tanks - Mature | Methane containment - limpet chambers. This is a standard technological intervention to trap methane gas Vacuum degassing - is a pump attached to a tank which withdraws gas from the sewage sludge reducing the residual emissions in the sludge and increasing its density. Commercial systems are relatively new and the magnitude of methane emissions reduction, net of the energy requirement to run the system remains yet to be published by commercial vendors who to date claim that the increased biogas yield through system installation is sufficient for operation of the plant and equipment. It remains to be seen how big an impact vacuum extraction will have on methane emissions as a component of wider proactive methane mitigation measures and its cost effectiveness. Covering of the post digestion storage tank and replacement of the post digestion aeration system. This is a standard technological intervention to trap methane gas. | Methane containment - high Vacuum degassing - medium Aeration - high | Containment of methane is proven for both coverings of tanks and limpet chambers. Vacuum degassing is a technical solution which, while there is no current data, would still be expected to capture methane. The net emisisons of running the vacuum chamber are not certain. Post-digestion aeration is a standard technological intervention. | Yes | This scheme is focused on bioresource for which the IED is the driver. | Fail | The scheme is considered to be driven by IED requirements. The scheme is considered to be driven by commercial benefit of capturing biogas for biomethane. | 4 |  |  |  | 5.069
| 5 | [14 empty] | Fail |  | 5 |  |  |  | 10.869
| 6 | [5 empty] | Environment team - OFW-OBQ-ANH-163.pdf - All Documents (sharepoint.com) | Request direction for finding further details of the sites and their specific interventions under each scheme | Covering of open digester limpet chambers to entrain gas Vacuum degassing of the digestate and connection to the gas header. Covering of the post digestion storage tank and connection to odour control. | Methane containment - mature Vacuum Degassing - TRL 7 - technology prototype demonstration in an operational environment Covering of tanks - Mature | Methane containment - limpet chambers. This is a standard technological intervention to trap methane gas Vacuum degassing - Commercial systems are relatively new and the magnitude of methane emissions reduction, net of the energy requirement to run the system remains yet to be published by commercial vendors who to date claim that the increased biogas yield through system installation is sufficient for operation of the plant and equipment. It remains to be seen how big an impact vacuum extraction will have on methane emissions as a component of wider proactive methane mitigation measures and its cost effectiveness. Covering of the post digestion storage tank and replacement of the post digestion aeration system. This is a standard technological intervention to trap methane gas. | Methane containment - high Vacuum degassing - medium | Containment of methane is proven for both coverings of tanks and limpet chambers. Vacuum degassing is a technical solution which, while there is no current data, would still be expected to capture methane. The net emisisons of running the vacuum chamber are not certain. | Yes | The Industrial Emissions Directive is a driver for capturing GHG pollution from this stage of the wastewater process (AAD, Dewatering etc). | Fail | The scheme is considered to be driven by IED requirements. The scheme is considered to be driven by commercial benefit of capturing biogas for biomethane either for consumption by the company or for export. | 6 |  |  |  | 2.915
| 7 | [5 empty] | Environment team - OFW-OBQ-ANH-163.pdf - All Documents (sharepoint.com) | Request direction for finding further details of the sites and their specific interventions under each scheme | Covering of open digester limpet chambers to entrain gas Vacuum degassing of the digestate and connection to the gas header. Connection of the covered post digestion storage tank to odour control. | Methane containment - mature Vacuum Degassing - TRL 7 - technology prototype demonstration in an operational environment Covering of tanks - Mature | Methane containment - limpet chambers. This is a standard technological intervention to trap methane gas Vacuum degassing - Commercial systems are relatively new and the magnitude of methane emissions reduction, net of the energy requirement to run the system remains yet to be published by commercial vendors who to date claim that the increased biogas yield through system installation is sufficient for operation of the plant and equipment. It remains to be seen how big an impact vacuum extraction will have on methane emissions as a component of wider proactive methane mitigation measures and its cost effectiveness Covering of the post digestion storage tank and replacement of the post digestion aeration system. This is a standard technological intervention to trap methane gas. | Methane containment - high Vacuum degassing - medium Aeration - high | Containment of methane is proven for both coverings of tanks and limpet chambers. Vacuum degassing is a technical solution which, while there is no current data, would still be expected to capture methane. The net emisisons of running the vacuum chamber are not certain. Post-digestion aeration is a standard technological intervention. | Yes | The Industrial Emissions Directive is a driver for capturing GHG pollution from this stage of the wastewater process (AAD, Dewatering etc). | Fail | The scheme is considered to be driven by IED requirements. The scheme is considered to be driven by commercial benefit of capturing biogas for biomethane either for consumption by the company or for export. | 7 |  |  |  | 2.078
| 8 | [5 empty] | Environment team - OFW-OBQ-ANH-163.pdf - All Documents (sharepoint.com) | Request direction for finding further details of the sites and their specific interventions under each scheme | Covering of open digester limpet chambers to entrain gas Vacuum degassing of the digestate and connection to the gas header. Covering of the post digestion storage tank, with appropriate safety systems to prevent over pressurisation of these tanks Connection to the gas header Replacement of the post digestion aeration system with gas mixing and the installation of a final stage of flash aeration (covered and odour controlled) prior to dewatering. | Methane containment - mature Vacuum Degassing - TRL 7 - technology prototype demonstration in an operational environment Covering of tanks - Mature | Methane containment - limpet chambers. This is a standard technological intervention to trap methane gas Vacuum degassing - Commercial systems are relatively new and the magnitude of methane emissions reduction, net of the energy requirement to run the system remains yet to be published by commercial vendors who to date claim that the increased biogas yield through system installation is sufficient for operation of the plant and equipment. It remains to be seen how big an impact vacuum extraction will have on methane emissions as a component of wider proactive methane mitigation measures and its cost effectiveness Covering of the post digestion storage tank and replacement of the post digestion aeration system. This is a standard technological intervention to trap methane gas. | Methane containment - high Vacuum degassing - medium Aeration - high | Containment of methane is proven for both coverings of tanks and limpet chambers. Vacuum degassing is a technical solution which, while there is no current data, would still be expected to capture methane. The net emisisons of running the vacuum chamber are not certain. Post-digestion aeration is a standard technological intervention. | Yes | The Industrial Emissions Directive is a driver for capturing GHG pollution from this stage of the wastewater process (AAD, Dewatering etc). | Fail | The scheme is considered to be driven by IED requirements. The scheme is considered to be driven by commercial benefit of capturing biogas for biomethane either for consumption by the company or for export. | 8 |  |  |  | 3.88
| 9 | [5 empty] | Environment team - OFW-OBQ-ANH-163.pdf - All Documents (sharepoint.com) | Request direction for finding further details of the sites and their specific interventions under each scheme | Interventions for Advanced Anaerobic Digesters at eight Sludge Treatment Centres (STC). The technology is a combination of different methods to maximise collection of methane, minimise leakage. Containment of the emissions. Covering of open digester limpet chambers to entrain gas Vacuum degassing of the digestate and connection to the gas header. Covering of the post digestion storage tank, with appropriate safety systems to prevent over pressurisation of these tanks Connection to the gas header Replacement of the post digestion aeration system with gas mixing and the installation of a final stage of flash aeration (covered and odour controlled) prior to dewatering. | Methane containment - mature Vacuum Degassing - TRL 7 - technology prototype demonstration in an operational environment Covering of tanks and aeration - Mature | Methane containment - limpet chambers. This is a standard technological intervention to trap methane gas Vacuum degassing - Commercial systems are relatively new and the magnitude of methane emissions reduction, net of the energy requirement to run the system remains yet to be published by commercial vendors who to date claim that the increased biogas yield through system installation is sufficient for operation of the plant and equipment. It remains to be seen how big an impact vacuum extraction will have on methane emissions as a component of wider proactive methane mitigation measures and its cost effectiveness Covering of the post digestion storage tank and replacement of the post digestion aeration system. This is a standard technological intervention to trap methane gas. | Methane containment - high Vacuum degassing - medium Aeration - high | Containment of methane is proven for both coverings of tanks and limpet chambers. Vacuum degassing is a technical solution which, while there is no current data, would still be expected to capture methane. The net emisisons of running the vacuum chamber are not certain. Post-digestion aeration is a standard technological intervention. | Yes | The Industrial Emissions Directive is a driver for capturing GHG pollution from this stage of the wastewater process (AAD, Dewatering etc). | Fail | The scheme is considered to be driven by IED requirements. The scheme is considered to be driven by commercial benefit of capturing biogas for biomethane either for consumption by the company or for export. | 9 |  |  |  | 3.813
| 10 | [5 empty] | Environment team - OFW-OBQ-ANH-163.pdf - All Documents (sharepoint.com) | Request direction for finding further details of the sites and their specific interventions under each scheme | Interventions for Advanced Anaerobic Digesters at eight Sludge Treatment Centres (STC). The technology is a combination of different methods to maximise collection of methane, minimise leakage. Containment of the emissions. Covering of open digester limpet chambers to entrain gas Vacuum degassing of the digestate and connection to the gas header. Covering of the post digestion storage tank, with appropriate safety systems to prevent over pressurisation of these tanks Connection to the gas header Replacement of the post digestion aeration system with gas mixing and the installation of a final stage of flash aeration (covered and odour controlled) prior to dewatering. | Methane containment - mature Vacuum Degassing - TRL 7 - technology prototype demonstration in an operational environment Covering of tanks and aeration - Mature | Methane containment - limpet chambers. This is a standard technological intervention to trap methane gas Vacuum degassing - Commercial systems are relatively new and the magnitude of methane emissions reduction, net of the energy requirement to run the system remains yet to be published by commercial vendors who to date claim that the increased biogas yield through system installation is sufficient for operation of the plant and equipment. It remains to be seen how big an impact vacuum extraction will have on methane emissions as a component of wider proactive methane mitigation measures and its cost effectiveness Covering of the post digestion storage tank and replacement of the post digestion aeration system. This is a standard technological intervention to trap methane gas. | Methane containment - high Vacuum degassing - medium Aeration - high | Containment of methane is proven for both coverings of tanks and limpet chambers. Vacuum degassing is a technical solution which, while there is no current data, would still be expected to capture methane. The net emisisons of running the vacuum chamber are not certain. Post-digestion aeration is a standard technological intervention. | Yes | The Industrial Emissions Directive is a driver for capturing GHG pollution from this stage of the wastewater process (AAD, Dewatering etc). | Fail | The scheme is considered to be driven by IED requirements. The scheme is considered to be driven by commercial benefit of capturing biogas for biomethane either for consumption by the company or for export. | 10 |  |  |  | 3.523
| 11 | [5 empty] | Environment team - OFW-OBQ-ANH-163.pdf - All Documents (sharepoint.com) | Request direction for finding further details of the sites and their specific interventions under each scheme | Interventions for Advanced Anaerobic Digesters at eight Sludge Treatment Centres (STC). The technology is a combination of different methods to maximise collection of methane, minimise leakage. Containment of the emissions. Covering of open digester limpet chambers to entrain gas Vacuum degassing of the digestate and connection to the gas header. Covering of the post digestion storage tank, with appropriate safety systems to prevent over pressurisation of these tanks Connection to the gas header Replacement of the post digestion aeration system with gas mixing and the installation of a final stage of flash aeration (covered and odour controlled) prior to dewatering. | Methane containment - mature Vacuum Degassing - TRL 7 - technology prototype demonstration in an operational environment Covering of tanks and aeration - Mature | Methane containment - limpet chambers. This is a standard technological intervention to trap methane gas Vacuum degassing - Commercial systems are relatively new and the magnitude of methane emissions reduction, net of the energy requirement to run the system remains yet to be published by commercial vendors who to date claim that the increased biogas yield through system installation is sufficient for operation of the plant and equipment. It remains to be seen how big an impact vacuum extraction will have on methane emissions as a component of wider proactive methane mitigation measures and its cost effectiveness Covering of the post digestion storage tank and replacement of the post digestion aeration system. This is a standard technological intervention to trap methane gas. | Methane containment - high Vacuum degassing - medium Aeration - high | Containment of methane is proven for both coverings of tanks and limpet chambers. Vacuum degassing is a technical solution which, while there is no current data, would still be expected to capture methane. The net emisisons of running the vacuum chamber are not certain. Post-digestion aeration is a standard technological intervention. | Yes | The Industrial Emissions Directive is a driver for capturing GHG pollution from this stage of the wastewater process (AAD, Dewatering etc). | Fail | The scheme is considered to be driven by IED requirements. The scheme is considered to be driven by commercial benefit of capturing biogas for biomethane either for consumption by the company or for export. | 11 |  |  |  | 4.047
| 12 | [5 empty] | Environment team - OFW-OBQ-ANH-163.pdf - All Documents (sharepoint.com) | Request direction for finding further details of the sites and their specific interventions under each scheme | Interventions for Advanced Anaerobic Digesters at eight Sludge Treatment Centres (STC). The technology is a combination of different methods to maximise collection of methane, minimise leakage. Containment of the emissions. Covering of open digester limpet chambers to entrain gas Vacuum degassing of the digestate and connection to the gas header. Covering of the post digestion storage tank, with appropriate safety systems to prevent over pressurisation of these tanks Connection to the gas header Replacement of the post digestion aeration system with gas mixing and the installation of a final stage of flash aeration (covered and odour controlled) prior to dewatering. | Methane containment - mature Vacuum Degassing - TRL 7 - technology prototype demonstration in an operational environment Covering of tanks and aeration - Mature | Methane containment - limpet chambers. This is a standard technological intervention to trap methane gas Vacuum degassing - Commercial systems are relatively new and the magnitude of methane emissions reduction, net of the energy requirement to run the system remains yet to be published by commercial vendors who to date claim that the increased biogas yield through system installation is sufficient for operation of the plant and equipment. It remains to be seen how big an impact vacuum extraction will have on methane emissions as a component of wider proactive methane mitigation measures and its cost effectiveness Covering of the post digestion storage tank and replacement of the post digestion aeration system. This is a standard technological intervention to trap methane gas. | Methane containment - high Vacuum degassing - medium Aeration - high | Containment of methane is proven for both coverings of tanks and limpet chambers. Vacuum degassing is a technical solution which, while there is no current data, would still be expected to capture methane. The net emisisons of running the vacuum chamber are not certain. Post-digestion aeration is a standard technological intervention. | Yes | The Industrial Emissions Directive is a driver for capturing GHG pollution from this stage of the wastewater process (AAD, Dewatering etc). | Fail | The scheme is considered to be driven by IED requirements. The scheme is considered to be driven by commercial benefit of capturing biogas for biomethane either for consumption by the company or for export. | 12 |  |  |  | 3.881
| 13 | [5 empty] | Environment team - OFW-OBQ-ANH-163.pdf - All Documents (sharepoint.com) | Request direction for finding further details of the sites and their specific interventions under each scheme | Interventions for Advanced Anaerobic Digesters at eight Sludge Treatment Centres (STC). The technology is a combination of different methods to maximise collection of methane, minimise leakage. Containment of the emissions. Cover the secondary activated sludge (SAS) holding tank | Covering of tanks - Mature | Covering of the secondary activated sludge holding tank. This is a standard technological intervention to trap methane gas. | Methane containment - high | Containment of methane is proven and a standard technological intervention. | Yes | The Industrial Emissions Directive is a driver for capturing GHG pollution from this stage of the wastewater process (AAD, Dewatering etc). | Fail | The scheme is considered to be driven by IED requirements. The scheme is considered to be driven by commercial benefit of capturing biogas for biomethane either for consumption by the company or for export. | 13 |  |  |  | 0.154
| 14 | ANH | CWW22.14 | Basildon STC Fugitive emissions N2O | Process emissions | Contain and treat - Covering and odour control of the anoxic and aeration tanks on the Amtreat plant. | Environment team - OFW-OBQ-ANH-163.pdf - All Documents (sharepoint.com) | Request direction for finding further details of the sites and their specific interventions under each scheme | Covering and odour control of the anoxic and aeration tanks on the Amtreat plant | Covering of tanks - Mature | Covering of tanks to capture N20 is an existing technological solution, innovation is limited. | Covering of tanks - High | Existing technology to contain GHGs | No | The scheme as to capture N2O at a Sewage Treatment Centre and addresses liquors. | Pass | The scheme will capture N2O emissions from assets. There is no wider benefit to undertaking this intervention other than to mitigate emissions. Innovation and learning is limited. | 14 | ANH | CWW22.14 | Basildon STC Fugitive emissions N2O | 1.562
| 15 | ANH | CWW22.15 | Colchester STC Fugitive emissions N2O | Process emissions | Contain and treat - Covering and odour control of the anoxic and aeration tanks on the Amtreat plant. | Environment team - OFW-OBQ-ANH-163.pdf - All Documents (sharepoint.com) | Request direction for finding further details of the sites and their specific interventions under each scheme | Covering and odour control of the anoxic and aeration tanks on the Amtreat plant | Covering of tanks - Mature | Covering of tanks to capture N20 is an existing technological solution, innovations is limited. | Covering of tanks - High | Existing technology to contain GHGs | No | The scheme as to capture N2O at a Sewage Treatment Centre and addresses liquors. | Pass | The scheme will capture N2O emissions from assets. There is no wider benefit to undertaking this intervention other than to mitigate emissions. Innovation and learning is limited. | 15 | ANH | CWW22.15 | Colchester STC Fugitive emissions N2O | 1.5
| 16 | ANH | CWW22.16 | Cliff Quay STC Fugitive emissions N2O | Process emissions | Contain and treat - Covering and odour control of the anoxic and aeration tanks on the Amtreat plant. | Environment team - OFW-OBQ-ANH-163.pdf - All Documents (sharepoint.com) | Request direction for finding further details of the sites and their specific interventions under each scheme | Covering and odour control of the anoxic and aeration tanks on the Amtreat plant | Covering of tanks - Mature | Covering of tanks to capture N20 is an existing technological solution, innovations is limited. | Covering of tanks - High | Existing technology to contain GHGs | No | The scheme as to capture N2O at a Sewage Treatment Centre and addresses liquors. | Pass | The scheme will capture N2O emissions from assets. There is no wider benefit to undertaking this intervention other than to mitigate emissions. Innovation and learning is limited. | 16 | ANH | CWW22.16 | Cliff Quay STC Fugitive emissions N2O | 1.606
| 17 | ANH | CWW22.17 | Whitlingham STC Fugitive Emissions N2O | Process emissions | Contain and treat - connection of liquor treatment plant to new odour control plant | Environment team - OFW-OBQ-ANH-163.pdf - All Documents (sharepoint.com) | Request direction for finding further details of the sites and their specific interventions under each scheme | Connection of covered liquor treatment plant to new odour control | Connectiong of treatment areas - Mature | Connection of covered liquor treament plant to new odour control is existing technology. | Covering of tanks - High | Existing technology to connect assets for GHG mitigation | Yes | This scheme is to connect a covered liquor treatment plant to Odour control, which is driven by the IED | Fail | This scheme is to address odour control which is driven by the IED. | 17 |  |  |  | 0.704
| 18 | ANH | CWW22.18 | Cotton Valley WRC Fugitive emissions N2O | Process emissions | Process modification to extend the anoxic zones to increase biodegradation and reduce N2O; and Real Time Control which includes the use of sensors and monitoring equipment including liquid and gas sensors. This monitoring is connected online monitoring and process control, such as adjusting air flow or ammonia-based aeration control (ABAC). The load can also be adjusted. This tends to require some infrastructure changes including adjustable nozzle upgrades for aeration blowers. | NA |  |  | Anoxic extension and aeration upgrade - low - TRL8 - actual technology completed and qualified through test and demonstration Real time control - Medium - TRL7 - technology prototype demonstration in an operational environment | Anoxic extension and aeration upgrade: No contribution to learning but could increase efficiency Real time control: developing technology, new technology for the sector and essential for N2O reductions | Anoxic extension and aeration upgrade - Medium Real time control - Medium | Anoxic extension and aeration upgrade: These are tried and tested technologies for implementation. Data is still being produced as the link between anoxic extension and N2O reductions. Aeration changes have shown reductions in N2O, however this can be offset by the increases in energy required for the aeration process. Real time control: likely to support reductions in emissions but can be offset by changes in energy demand for aeration to reduce N2O. | No | The scheme is to driven by N2O mitigation and not affected by IED | Pass | Representations referenced digital integration, a threshold requirement for innovation, learning, and efficiency. Schemes meet the innovation threshold due to absence of schemes in the UK, and requirement for piloting. Monitoring is not standard practice in the industry, especially not with control. | 18 | ANH | CWW22.18 | Cotton Valley WRC Fugitive emissions N2O | 5.871
| 19 | ANH | CWW22.19 | Great Billing WRC Fugitive Emissions N2O | Process emissions | Enhanced aeration is a process modification to increase air flow for aerobic biodegradation. Real Time Control includes the use of sensors and monitoring equipment including liquid and gas sensors. This monitoring is connected online monitoring and process control, such as adjusting air flow or ammonia-based aeration control (ABAC). The load can also be adjusted. This tends to require some infrastructure changes including adjustable nozzle upgrades for aeration blowers. | NA |  |  | Anoxic extension and aeration upgrade - low - TRL8 - actual technology completed and qualified through test and demonstration Real time control - Medium - TRL7 - technology prototype demonstration in an operational environment | Anoxic extension and aeration upgrade: No contribution to learning but could increase efficiency Real time control: developing technology, new technology for the sector and essential for N2O reductions | Anoxic extension and aeration upgrade - Medium Real time control - Medium | Anoxic extension and aeration upgrade: These are tried and tested technologies for implementation. Data is still being produced as the link between anoxic extension and N2O reductions. Aeration changes have shown reductions in N2O, however this can be offset by the increases in energy required for the aeration process. Real time control: likely to support reductions in emissions but can be offset by changes in energy demand for aeration to reduce N2O. | No | The scheme is to driven by N2O mitigation and not affected by IED | Pass | Representations referenced digital integration, a threshold requirement for innovation, learning, and efficiency. Schemes meet the innovation threshold due to absence of schemes in the UK, and requirement for piloting. Monitoring is not standard practice in the industry, especially not with control. | 19 | ANH | CWW22.19 | Great Billing WRC Fugitive Emissions N2O | 10.546
| 20 | ANH | CWW22.20 | Basildon WRC Fugitive Emissions N2O | Process emissions | Anoxic extension is a process modification to extend the anoxic zones to increase biodegradation and reduce N2O. Aeration upgrade is a process modification to increase air flow for aerobic biodegradation. Real Time Control includes the use of sensors and monitoring equipment including liquid and gas sensors. This monitoring is connected online monitoring and process control, such as adjusting air flow or ammonia-based aeration control (ABAC). The load can also be adjusted. This tends to require some infrastructure changes including adjustable nozzle upgrades for aeration blowers. | NA |  |  | Anoxic extension and aeration upgrade - low - TRL8 - actual technology completed and qualified through test and demonstration Real time control - Medium - TRL7 - technology prototype demonstration in an operational environment | Anoxic extension and aeration upgrade: No contribution to learning but could increase efficiency Real time control: developing technology, new technology for the sector and essential for N2O reductions | Anoxic extension and aeration upgrade - Medium Real time control - Medium | Anoxic extension and aeration upgrade: These are tried and tested technologies for implementation. Data is still being produced as the link between anoxic extension and N2O reductions. Aeration changes have shown reductions in N2O, however this can be offset by the increases in energy required for the aeration process. Real time control: likely to support reductions in emissions but can be offset by changes in energy demand for aeration to reduce N2O. | No | The scheme is to driven by N2O mitigation and not affected by IED | Pass | Representations referenced digital integration, a threshold requirement for innovation, learning, and efficiency. Schemes meet the innovation threshold due to absence of schemes in the UK, and requirement for piloting. Monitoring is not standard practice in the industry, especially not with control. | 20 | ANH | CWW22.20 | Basildon WRC Fugitive Emissions N2O | 2.778
| 21 | ANH | CWW22.21 | Bedford WRC Fugitive Emissions N2O | Process emissions | Diffuser upgrade to modify the aeration supplied to the wastewater load. Real Time Control includes the use of sensors and monitoring equipment including liquid and gas sensors. This monitoring is connected online monitoring and process control, such as adjusting air flow or ammonia-based aeration control (ABAC). The load can also be adjusted. This tends to require some infrastructure changes including adjustable nozzle upgrades for aeration blowers. | NA |  |  | Real Time Control - Medium - TRL 7 - technology prototype demonstration in an operational environment Aeration upgrade - Low | Real time control: developing technology, new technology for the sector and essential for N2O reductions Aeration upgrade: Change of diffusers makes limited contribution to learning but could increase efficiency | Anoxic extension and aeration upgrade - Medium Real time control - Medium | Anoxic extension and aeration upgrade: These are tried and tested technologies for implementation. Data is still being produced as the link between anoxic extension and N2O reductions. Aeration changes have shown reductions in N2O, however this can be offset by the increases in energy required for the aeration process. Real time control: likely to support reductions in emissions but can be offset by changes in energy demand for aeration to reduce N2O. | No | The scheme is to driven by N2O mitigation and not affected by IED | Pass | Representations referenced digital integration, a threshold requirement for innovation, learning, and efficiency. Schemes meet the innovation threshold due to absence of schemes in the UK, and requirement for piloting. Monitoring is not standard practice in the industry, especially not with control. | 21 | ANH | CWW22.21 | Bedford WRC Fugitive Emissions N2O | 1.133
| 22 | ANH | CWW22.22 | Kings Lynn WRC Fugitive Emissions N2O | Process emissions | Real Time Control includes the use of sensors and monitoring equipment including liquid and gas sensors. This monitoring is connected online monitoring and process control, such as adjusting air flow or ammonia-based aeration control (ABAC). The load can also be adjusted. This tends to require some infrastructure changes including adjustable nozzle upgrades for aeration blowers. | NA |  |  | Real Time Control - Medium - TRL 7 - technology prototype demonstration in an operational environment | Real time control: developing technology, new technology for the sector and essential for N2O reductions | Real time control - Medium | Real time control: control of process variables expected to support reductions in emissions but can be offset by changes in energy demand for aeration to reduce N2O. | No | The scheme is to driven by N2O mitigation and not affected by IED | Pass | Representations referenced digital integration, a threshold requirement for innovation, learning, and efficiency. Schemes meet the innovation threshold due to absence of schemes in the UK, and requirement for piloting. Monitoring is not standard practice in the industry, especially not with control. | 22 | ANH | CWW22.22 | Kings Lynn WRC Fugitive Emissions N2O | 0.952
| 23 | ANH | CWW22.23 | Newton Marsh WRC Fugitive Emissions N2O | Process emissions | Real Time Control includes the use of sensors and monitoring equipment including liquid and gas sensors. This monitoring is connected online monitoring and process control, such as adjusting air flow or ammonia-based aeration control (ABAC). The load can also be adjusted. This tends to require some infrastructure changes including adjustable nozzle upgrades for aeration blowers. | NA |  |  | Real Time Control - Medium - TRL 7 - technology prototype demonstration in an operational environment | Real time control: developing technology, new technology for the sector and essential for N2O reductions | Real time control - Medium | Real time control: control of process variables expected to support reductions in emissions but can be offset by changes in energy demand for aeration to reduce N2O. | No | The scheme is to driven by N2O mitigation and not affected by IED | Pass | Representations referenced digital integration, a threshold requirement for innovation, learning, and efficiency. Schemes meet the innovation threshold due to absence of schemes in the UK, and requirement for piloting. Monitoring is not standard practice in the industry, especially not with control. | 23 | ANH | CWW22.23 | Newton Marsh WRC Fugitive Emissions N2O | 0.447
| 24 | ANH | CWW22.24 | Broadholme WRC Fugitive Emissions N2O | Process emissions | Diffuser upgrade to modify the aeration supplied to the wastewater load in the Activated Sludge Process. Real Time Control includes the use of sensors and monitoring equipment including liquid and gas sensors. This monitoring is connected online monitoring and process control, such as adjusting air flow or ammonia-based aeration control (ABAC). The load can also be adjusted. This tends to require some infrastructure changes including adjustable nozzle upgrades for aeration blowers. | Environment team - OFW-OBQ-ANH-067.pdf - All Documents (sharepoint.com) | Request to understand how it differs from a WINEP scheme |  | Real Time Control - Medium - TRL 7 - technology prototype demonstration in an operational environment Aeration upgrade - Low | Real time control: developing technology, new technology for the sector and essential for N2O reductions Aeration upgrade: Change of diffusers makes limited contribution to learning but could increase efficiency | Real time control - Medium | Real time control: control of process variables expected to support reductions in emissions but can be offset by changes in energy demand for aeration to reduce N2O. | No | The scheme is to driven by N2O mitigation and not affected by IED | Pass | Representations referenced digital integration, a threshold requirement for innovation, learning, and efficiency. Schemes meet the innovation threshold due to absence of schemes in the UK, and requirement for piloting. Monitoring is not standard practice in the industry, especially not with control. | 24 | ANH | CWW22.24 | Broadholme WRC Fugitive Emissions N2O | 0.727
| 25 | ANH | CWW22.25 | Letchworth WRC Fugitive emissions N2O | Process emissions | Membrane Aerated Biofilm Reactors impact Net Zero by reducing energy demand of forced aeration treatments but could also be associated with significantly reduced nitrous oxide (N2O) process emissions. The MABR is supported by upgrades to Aeration and RTC. | NA |  |  | MABR - Medium - TRL 7 - technology prototype demonstration in an operational environment Real Time Control - Medium - TRL 7 - technology prototype demonstration in an operational environment Aeration upgrade - Low | MABR considered a market ready solution showing promising results. This is technology provides an opportunity for learning and relatively easy retrofitting in the incidence it is found sufficiently effective. Real time control: developing technology, new technology for the sector and essential for N2O reductions Aeration upgrade: Change of diffusers makes limited contribution to learning but could increase efficiency | Real time control - Medium Aeration upgrade - Medium MABR - Medium | MABR: The Net Zero Technology Review has shown there is some limited evidence for N2O reductions. Sevent Trent Water has reported reductions in trialling MABR for another purpose and a Danish company has corroborated these findings. Real time control: control of process variables expected to support reductions in emissions but can be offset by changes in energy demand for aeration to reduce N2O. Aeration upgrade: Aeration changes have shown reductions in N2O, however this can be offset by the increases in energy required for the aeration process. | No | The scheme is to driven by N2O mitigation and not affected by IED | Pass | Membrane aerated biofilm reactor (MABR) represents a new technology at the deployment level. Learning from this innovation could provide substantial emissions reductions across the sector if successful due to the retrofit capability of the technology. | 25 | ANH | CWW22.25 | Letchworth WRC Fugitive emissions N2O | 11.355
| 26 | ANH | CWW22.26 | Newmarket WRC Fugitive Emissions N2O | Process emissions | Membrane Aerated Biofilm Reactors impact Net Zero by reducing energy demand of forced aeration treatments but could also be associated with significantly reduced nitrous oxide (N2O) process emissions. The MABR is supported by upgrades to Aeration and RTC. | OFW-OBQ-ANH-188.pdf | To understand why this scheme and 22.28 appear more expensive under a unit cost analysis than schemes 22.25 and 22.29 |  | MABR - Medium - TRL 7 - technology prototype demonstration in an operational environment Real Time Control - Medium - TRL 7 - technology prototype demonstration in an operational environment Aeration upgrade - Low | MABR considered a market ready solution showing promising results. This is technology provides an opportunity for learning and relatively easy retrofitting in the incidence it is found sufficiently effective. Real time control: developing technology, new technology for the sector and essential for N2O reductions Aeration upgrade: Change of diffusers makes limited contribution to learning but could increase efficiency | Real time control - Medium Aeration upgrade - Medium MABR - Medium | MABR: The Net Zero Technology Review has shown there is some limited evidence for N2O reductions. Sevent Trent Water has reported reductions in trialling MABR for another purpose and a Danish company has corroborated these findings. Real time control: control of the process variables is expected to support reductions in emissions but can be offset by changes in energy demand for aeration to reduce N2O. Aeration upgrade: Aeration changes have shown reductions in N2O, however this can be offset by the increases in energy required for the aeration process. | No | The scheme is to driven by N2O mitigation and not affected by IED | Pass | Membrane aerated biofilm reactor (MABR) represents a new technology at the deployment level. Learning from this innovation could provide substantial emissions reductions across the sector if successful due to the retrofit capability of the technology. | 26 | ANH | CWW22.26 | Newmarket WRC Fugitive Emissions N2O | 4.608
| 27 | ANH | CWW22.27 | Hitchin WRC Fugitive emissions N2O | Process emissions | Anoxic extension is a process modification to extend the anoxic zones to increase biodegradation and reduce N2O. Real Time Control includes the use of sensors and monitoring equipment including liquid and gas sensors. This monitoring is connected to online monitoring and process control, such as adjusting air flow or ammonia-based aeration control (ABAC). The load can also be adjusted. This tends to require some infrastructure changes including adjustable nozzle upgrades for aeration blowers. | NA |  |  | Anoxic extension and aeration upgrade - low - TRL8 - actual technology completed and qualified through test and demonstration Real time control - Medium - TRL7 - technology prototype demonstration in an operational environment | Anoxic extension and aeration upgrade: No contribution to learning but could increase efficiency Real time control: developing technology, new technology for the sector and essential for N2O reductions | Anoxic extension and aeration upgrade - Medium Real time control - Medium | Anoxic extension and aeration upgrade: These are tried and tested technologies for implementation. Data is still being produced as the link between anoxic extension and N2O reductions. Aeration changes have shown reductions in N2O, however this can be offset by the increases in energy required for the aeration process. Real time control: likely to support reductions in emissions but can be offset by changes in energy demand for aeration to reduce N2O. | No | The scheme is to driven by N2O mitigation and not affected by IED | Pass | Representations referenced digital integration, a threshold requirement for innovation, learning, and efficiency. Schemes meet the innovation threshold due to absence of schemes in the UK, and requirement for piloting. Monitoring is not standard practice in the industry, especially not with control. | 27 | ANH | CWW22.27 | Hitchin WRC Fugitive emissions N2O | 1.402
| 28 | ANH | CWW22.28 | Dunstable WRC Fugitive Emissions N2O | Process emissions | Membrane Aerated Biofilm Reactors impact Net Zero by reducing energy demand of forced aeration treatments but could also be associated with significantly reduced nitrous oxide (N2O) process emissions. The MABR is supported by upgrades to Aeration and RTC. | OFW-OBQ-ANH-188.pdf | To understand why this scheme and 22.26 appear more expensive under a unit cost analysis than schemes 22.25 and 22.29 |  | MABR - Medium - TRL 7 - technology prototype demonstration in an operational environment Real Time Control - Medium - TRL 7 - technology prototype demonstration in an operational environment Aeration upgrade - Low | MABR considered a market ready solution showing promising results. This is technology provides an opportunity for learning and relatively easy retrofitting in the incidence it is found sufficiently effective. Real time control: developing technology, new technology for the sector and essential for N2O reductions Aeration upgrade: Change of diffusers makes limited contribution to learning but could increase efficiency | Real time control - Medium Aeration upgrade - Medium MABR - Medium | MABR: The Net Zero Technology Review has shown there is some limited evidence for N2O reductions. Sevent Trent Water has reported reductions in trialling MABR for another purpose and a Danish company has corroborated these findings. Real time control: control of the process variables is expected to support reductions in emissions but can be offset by changes in energy demand for aeration to reduce N2O. Aeration upgrade: Aeration changes have shown reductions in N2O, however this can be offset by the increases in energy required for the aeration process. | No | The scheme is to driven by N2O mitigation and not affected by IED | Pass | Membrane aerated biofilm reactor (MABR) represents a new technology at the deployment level. Learning from this innovation could provide substantial emissions reductions across the sector if successful due to the retrofit capability of the technology. | 28 | ANH | CWW22.28 | Dunstable WRC Fugitive Emissions N2O | 12.301
| 29 | ANH | CWW22.29 | Flitwick WRC Fugitive Emissions N2O | Process emissions | Membrane Aerated Biofilm Reactors impact Net Zero by reducing energy demand of forced aeration treatments but could also be associated with significantly reduced nitrous oxide (N2O) process emissions. The MABR is supported by upgrades to Aeration and RTC. | NA |  |  | MABR - Medium - TRL 7 - technology prototype demonstration in an operational environment Real Time Control - Medium - TRL 7 - technology prototype demonstration in an operational environment Aeration upgrade - Low | MABR considered a market ready solution showing promising results. This is technology provides an opportunity for learning and relatively easy retrofitting in the incidence it is found sufficiently effective. Real time control: developing technology, new technology for the sector and essential for N2O reductions Aeration upgrade: Change of diffusers makes limited contribution to learning but could increase efficiency | Real time control - Medium Aeration upgrade - Medium MABR - Medium | MABR: The Net Zero Technology Review has shown there is some limited evidence for N2O reductions. Sevent Trent Water has reported reductions in trialling MABR for another purpose and a Danish company has corroborated these findings. Real time control: control of the process variables is expected to support reductions in emissions but can be offset by changes in energy demand for aeration to reduce N2O. Aeration upgrade: Aeration changes have shown reductions in N2O, however this can be offset by the increases in energy required for the aeration process. | No | The scheme is to driven by N2O mitigation and not affected by IED | Pass | Membrane aerated biofilm reactor (MABR) represents a new technology at the deployment level. Learning from this innovation could provide substantial emissions reductions across the sector if successful due to the retrofit capability of the technology. | 29 | ANH | CWW22.29 | Flitwick WRC Fugitive Emissions N2O | 6.453
| 30 | [5 empty] | OFW-OBQ-ANH-163.pdf | Request direction for finding further details of the sites and their specific interventions under each scheme | Installation of a traditional liquor treatment plant. It includes a high rate activated sludge process with the addition of an external carbon source, pumping of flows in and out of the process and the covering and odour control of the process tanks | [6 empty] | Fail | Scheme proposes to construct a new liquor treatment plant, this is Base allowance. | 30 |  |  |  | 7.379
| 31 | [14 empty] | Fail |  | 31 |  |  |  | 0.159
| 32 | [14 empty] | Fail |  | 32 |  |  |  | 0.873
| 33 | [14 empty] | Fail |  | 33 |  |  |  | 1.307
| 34 | [14 empty] | Fail |  | 34 |  |  |  | 1.356
| 35 | [14 empty] | Fail |  | 35 |  |  |  | 3.922
| 36 | ANH | CWW22.36 | Huntingdon WRC Fugitive Emissions N2O | Process emissions | Enhanced aeration is a process modification to increase air flow for aerobic biodegradation. Real Time Control includes the use of sensors and monitoring equipment including liquid and gas sensors. This monitoring is connected online monitoring and process control, such as adjusting air flow or ammonia-based aeration control (ABAC). The load can also be adjusted. This tends to require some infrastructure changes including adjustable nozzle upgrades for aeration blowers. | NA |  |  | Real Time Control - Medium - TRL 7 - technology prototype demonstration in an operational environment Aeration upgrade - Low | Real time control: developing technology, new technology for the sector and essential for N2O reductions Aeration upgrade: Change of diffusers makes limited contribution to learning but could increase efficiency | Real time control - Medium Aeration upgrade - Medium | Real time control: control of the process variables is expected to support reductions in emissions but can be offset by changes in energy demand for aeration to reduce N2O. Aeration upgrade: Aeration changes have shown reductions in N2O, however this can be offset by the increases in energy required for the aeration process. | No | Solution is designed for the wastewater treatment stage prior to bioresources treatment | Pass | Representations referenced digital integration, a threshold requirement for innovation, learning, and efficiency. Schemes meet the innovation threshold due to absence of schemes in the UK, and requirement for piloting. Monitoring is not standard practice in the industry, especially not with control. | 36 | ANH | CWW22.36 | Huntingdon WRC Fugitive Emissions N2O | 2.791
| 37 | [14 empty] | Fail |  | 37 |  |  |  | 7.681
| 38 | [14 empty] | Fail |  | 38 |  |  |  | 12.766
| 39 | [14 empty] | Fail |  | 39 |  |  |  | 14.328
| 40 | [14 empty] | Fail |  | 40 |  |  |  | 14.088
| 41 | [14 empty] | Fail |  | 41 |  |  |  | 14.165
| 42 | [14 empty] | Fail |  | 42 |  |  |  | 14.672
| 43 | [5 empty] | NA |  |  | Real Time Control - Medium - TRL 7 - technology prototype demonstration in an operational environment | Real time control: developing technology, new technology for the sector and essential for N2O reductions | Real time control - Medium | Real time control: control of the process variables is expected to support reductions in emissions but can be offset by changes in energy demand for aeration to reduce N2O. | No | Solution is designed for the wastewater treatment stage prior to bioresources treatment | Fail | This scheme proposes using technology which is represents an improvement in operations of the asset. This comes under general maintenance and Base spending. | 43 |  |  |  | 0.967
| 44 | [5 empty] | NA |  |  | Real Time Control - Medium - TRL 7 - technology prototype demonstration in an operational environment | Real time control: developing technology, new technology for the sector and essential for N2O reductions | Real time control - Medium | Real time control: control of the process variables is expected to support reductions in emissions but can be offset by changes in energy demand for aeration to reduce N2O. | No | Solution is designed for the wastewater treatment stage prior to bioresources treatment | Fail | This scheme proposes using technology which is represents an improvement in operations of the asset. This comes under general maintenance and Base spending. | 44 |  |  |  | 1.662
| 45 | ANH | CWW22.45 | Colchester WRC Fugitive Emissions N2O | Process emissions | Membrane Aerated Biofilm Reactor is a technology which combines high nutrient removal and energy efficiency compared to traditional systems. It enables simultaneous nitrification-denitrification in a single tank and produce a high-quality effluent. They can reduce aeration energy use significantly. The MABR is supported by upgrades to Aeration and RTC. | NA |  |  | MABR - Medium - TRL 7 - technology prototype demonstration in an operational environment Real Time Control - Medium - TRL 7 - technology prototype demonstration in an operational environment | MABR considered a market ready solution showing promising results. This is technology provides an opportunity for learning and relatively easy retrofitting in the incidence it is found sufficiently effective. Real time control: developing technology, new technology for the sector and essential for N2O reductions | Real time control - Medium MABR - Medium | MABR: The Net Zero Technology Review has shown there is some limited evidence for N2O reductions. SVE has reported reductions in trialling MABR for another purpose and a Danish company has corroborated these findings. Real time control: likely to support reductions in emissions but can be offset by changes in energy demand for aeration to reduce N2O. | No | Solution is designed for the wastewater treatment stage prior to bioresources treatment | Pass | MABR represents a new technology at the deployment level. Learning from this innovation could provide substantial emissions reductions across the sector if successful due to the retrofit capability of the technology. | 45 | ANH | CWW22.45 | Colchester WRC Fugitive Emissions N2O | 10.466
| 46 | HDD | CWW22.1 | Process Emissions Reduction | Process emissions | (HDD clarification) A digital twin is a virtual replica of a physical system, process, or product that can be used to simulate, predict, and optimise its performance. In the context of wastewater treatment works, a digital twin will be used to create a detailed model of the entire treatment process, from the inflow of wastewater to the discharge of treated water using a combination of mechanistic models and machine learning. This model can be used to simulate the behaviour of the system under different conditions, optimise the performance of the treatment process, and predict the impact of changes to the system. We intend to use the digital twin system to both reduce the creation and release of harmful greenhouse gases. ASP Cover & Treat to reduce N2O production - Welshpool site | OFW-OBQ-HDD-081 Response.pdf | To understand the scheme in greater detail due to difficulty in interpreting HDD narrative documents and because of percieved contradictions across documents regarding submission of an Enhancement Case. | A digital twin solution, combined with cover of the ASP and treatment of N2O on the Welshpool site to enable net zero. (HDD) A digital twin is a virtual replica of a physical system, process, or product that can be used to simulate, predict, and optimise its performance. In the context of wastewater treatment works, a digital twin will be used to create a detailed model of the entire treatment process, from the inflow of wastewater to the discharge of treated water using a combination of mechanistic models and machine learning. This model can be used to simulate the behaviour of the system under different conditions, optimise the performance of the treatment process, and predict the impact of changes to the system. We intend to use the digital twin system to both reduce the creation and release of harmful greenhouse gases. | Digital Twin - Low - TRL 8 - actual technology completed and qualified through test and demonstration Containment of N2O emissions on ASP - Low | A digital representation of complex treatment trains or whole treatment works. Can be used to drive efficiency and associated emissions reduction but depends on the type of digital twin. Digital twins are not considered a net zero technology in and of themselves (Net Zero Technology Review), however, the application of machine learning and Artificial Intelligence to a Digital Twin poses a much greater opportunity for process optimisation for emissions reductions and energy consumption. Containment of emissions on the Activated Sludge Process is a standard technological intervention. | Digital Twins - Medium Covering of ASP - High | Digitial Twins are not a new technology or specifically a net zero technology. As with Real Time Control, the expectation is that control of the process variables will enable better outputs in terms of emissions and make more efficient use of energy. The understanding is that machine learning can optimise processes to a greater degree than Real Time Control and manage assets of greater complexity. Containment of emissions by covering the Activated Sludge Process is a standard technological solution. | No | Solution is designed for the wastewater treatment stage prior to bioresources treatment | Pass | Digital Twins are a technological solution which goes beyond current implementation in the water sector. It presents an opportunity for sector learning and deployment of innovation in the realm of Digital Twins which could create emissions reductions and efficiency. | 46 | HDD | CWW22.1 | Process Emissions Reduction | 0.864
| 47 | [7 empty] | the Welshpool site to enable net zero. | [6 empty] | Fail |  | 47 |  |  |  | 0.038
| 48 | SVE | NZ#1 | Digital Twin | Process emissions | Digital Twin uses artificial intelligence, machine learning and mechanistic models to optimise the processes. Digital Twin has been identified for larger, more complex and dynamic processes. (SVE) [Digital Twin] can be described as real-time control, but we believe it represents the pinnacle of what is technically achievable and that all real-time control systems cannot considered to be equivalent. | Environment team - OFW-OBQ-SVE-173 response FINAL.pdf - All Documents (sharepoint.com); OFW-OBQ-SVE-041 Response.pdf | Ref 173: To understand better the justification for the costs associated with Digital Twins and how these are calculated for the sites identified. It also sought to understand the difference between Digital Twin technology and Real Time Control (RTC) Ref 41: To clarify costs involved in schemes in the submission of the BPT | Ref 173: This uses existing instrumentation and mechanical equipment to allow optimum control of the treatment works using a new control system based upon both mechanistic models of wastewater treatment and machine learning. [Digital Twin] can be described as real-time control, but we believe it represents the pinnacle of what is technically achievable and that all real-time control systems cannot considered to be equivalent. Ref 41: SVE agreed to make updates to submission of SBT | Digital Twin - Low - TRL 8 - actual technology completed and qualified through test and demonstration | A digital representation of complex treatment trains or whole treatment works. Can be used to drive efficiency and associated emissions reduction but depends on the type of digital twin. Digital twins are not considered a net zero technology in and of themselves (Net Zero Technology Review), however, the application of machine learning and Artificial Intelligence to a Digital Twin poses a much greater opportunity for process optimisation for emissions reductions and energy consumption. | Digital Twins - Medium | Digitial Twins are not a new technology or specifically a net zero technology. As with Real Time Control, the expectation is that control of the process variables will enable better outputs in terms of emissions and make more efficient use of energy. The understanding is that machine learning can optimise processes to a greater degree than Real Time Control and manage assets of greater complexity. | No | Solution is designed for the wastewater treatment stage prior to bioresources treatment | Pass | Digital Twins are a technological solution which goes beyond current implementation in the water sector. It presents an opportunity for sector learning and deployment of innovation in the realm of Digital Twins which could create emissions reductions and efficiency. | 48 | SVE | NZ#1 | Digital Twin | 53.341
| 49 | SVE | NZ#2 | Cover & Treat | Process emissions | Containment, or cover and treatment, of emissions involves building an impermeable canopy over wastewater treatment works to capture N2O emitted by activated sludge plants. The N2O is treated using a photocatalytic membrane which breaks down the gas into N2 and O2. |  | See Ref 41, above See Ref 83, below |  | Photocatalytic Membrane - Medium | The photocatalytic membrane has been in development since 2002. The proposal is for trialling and learning to understand if the membrane is effective in deployment at field scale. The schemes present an opportunity for learning and innovation. | Photocatalytic Membrane - Medium Covering of ASP - Low | There is a risk the trials of containment will not deliver emission reductions, however this technology has been developed over 20 years with evidence leading to this point for field trials. Covering of ASP - Standard technological intervention. | No | Solution is designed for the wastewater treatment stage prior to bioresources treatment | Pass | The deployment of the Photocatalytic Membrate is novel in the wastewater sector and presents an opportunity for sector learning and innovation. | 49 | SVE | NZ#2 | Cover & Treat | 92.895
| 50 | SVE | NZ#3 | ASP Intensification | Process emissions | Membrane Aerated Biofilm Reactor is a technology which combines high nutrient removal and energy efficiency compared to traditional systems. It enables simultaneous nitrification-denitrification in a single tank and produce a high-quality effluent. They can reduce aeration energy use significantly. The MABR is supported by upgrades to Aeration and RTC. | Environment team - OFW-OBQ-SVE-083 Response.pdf - All Documents (sharepoint.com) | Ref 83: Confirmation of values for GHG data Ref 41: See above | Ref 83: SVE agreed to update tables OUT4 and OUT5 to use comparable emissions data to other companes. SVE provided an explanation of their emissions factors for N2O, these have been used for table CWW22 technologies for N2O abatement. Description of technology: By using membrane aeration in anoxic or aerated zones, trials of MABR have shown extremely low levels of N2O production. The addition of MABR cassettes to an existing ASP gives additional treatment capacity. We are also investigating other intensification options. From Query: As previously articulated, we originally updated the CAW17 assumptions around nitrous oxide in line with the functionality built into the workbook. Our updates were based on observed, measured data that we consider more closely aligns to the real-world impact of these greenhouse gases. | MABR - Medium - TRL 7 - technology prototype demonstration in an operational environment | MABR is considered a market ready solution showing promising results. This technology provides an opportunity for learning and relatively easy retrofitting in the incidence it is found sufficiently effective. | MABR - Medium | The Net Zero Technology Review has shown there is some limited evidence for N2O reductions. SVE have happened upon reductions in trialling MABR for another purpose and a Danish company has corroborated these findings. | No | Solution is designed for the wastewater treatment stage prior to bioresources treatment | Pass | MABR represents a new technology at the deployment level. Learning from this innovation could provide substantial emissions reductions across the sector if successful due to the retrofit capability of the technology. | 50 | SVE | NZ#3 | ASP Intensification | 104.111
| 51 | SVE | NZ#4 | Active gas capture | Process emissions | More effective digestion and removal of CH4 in the digester vessels, resulting in less carryover into downstream tanks. Digestate is then passed through a vacuum degassing process to remove any remaining traces of methane | OFW-REP-SVE-114 response.pdf | See Ref 41 above Query 114 requested the separation of vacuum degassing and in-series digestion in the costs and benefits of this scheme. | Ref 114: SVE provided cost and benefit figures separately for vacuum degassing and in-series digesters. | Vacuum Degassing - TRL 7 - technology prototype demonstration in an operational environment Series digester - low - this technology has been deployed and tested. | Vacuum degassing: It is considered a newer technology but is unlikely to fulfil requirements for innovation. Trials completed in 2020-2025. Vacuum degassing - is a pump attached to a tank which withdraws gas from the sewage sludge reducing the residual emissions in the sludge and increasing its density. Commercial systems are relatively new. The magnitude of methane emissions reduction, net of the energy requirement to run the system, remains to be published by commercial vendors who to date claim that the increased biogas yield through system installation is sufficient for operation of the plant and equipment. It remains to be seen how big an impact vacuum extraction will have on methane emissions as a component of wider proactive methane mitigation measures and its cost effectiveness. Covering of the post digestion storage tank and replacement of the post digestion aeration system: This is a standard technological intervention to trap methane gas. Series digesters: Few existing schemes in 2020-2025. Reduction in redundancy and potentially efficiency as a result minimised time for maintenance | Vacuum degassing - medium Series digester - medium | Vacuum degassing: is a technical solution which, while there is no current data, would still be expected to capture methane. The net emisisons of running the vacuum chamber are not certain. Post-digestion aeration is a standard technological intervention. Series digester: the process involves relatively simple engineering to re-plum the digester | Yes | At Draft Determinations the Industrial Emissions Directive was considered to be the driver for this scheme. After reviewing representations and the IED terms, this scheme is not considered to be driven by the IED. | Pass | Vacuum degassing removes methane from sludge as it leaves the digester. The IED affects only the capture of methane from tanks. VD can demonstrate innovation and is expected to be revenue neutral. Series digester upgrades will likely help with redundancy and operation of the asset. This is a base cost. | 51 | SVE | NZ#4 | Active gas capture | 35.621
| 52 | [14 empty] | Fail |  | 52 |  |  |  | 0.72
| 53 | [14 empty] | Fail |  | 53 |  |  |  | 6.358
| 54 | [14 empty] | Fail |  | 54 |  |  |  | 0.271
| 55 | SVE | NZ#8 | Cellulose recovery | Fossil fuel reduction | Cellulose recovery to use it to heat the biomass boilers, typically thermal hydrolysis sludge treatment. | [9 empty] | Fail |  | 55 |  |  |  | 63.075
| 56 | SVE | NZ#9 | Process Optimisation | Process emissions | Instrumentation & optimisation to reduce N2O production. Real Time Control includes the use of sensors and monitoring equipment including liquid and gas sensors. This monitoring is connected online monitoring and process control, such as adjusting air flow or ammonia-based aeration control (ABAC). The load can also be adjusted. This tends to require some infrastructure changes including adjustable nozzle upgrades for aeration blowers. | NA | See Ref 83, above |  | Real Time Control - Medium - TRL 7 - technology prototype demonstration in an operational environment | Real time control: developing technology, new technology for the sector and essential for N2O reductions | Real time control - Medium | Real time control: control of the process variables is expected to support reductions in emissions but can be offset by changes in energy demand for aeration to reduce N2O. | No | The scheme is driven by N2O mitigation and not affected by IED | Pass | Representations referenced digital integration, a threshold requirement for innovation, learning, and efficiency. Schemes meet the innovation threshold due to absence of schemes in the UK, and requirement for piloting. Monitoring is not standard practice in the industry, especially not with control. | 56 | SVE | NZ#9 | Process Optimisation | 8.967
| 57 | [14 empty] | Fail |  | 57 |  |  |  | 1.611
| 58 | [14 empty] | Fail |  | 58 |  |  |  | 3.711
| 59 | [14 empty] | Fail |  | 59 |  |  |  | 3.285
| 60 | [14 empty] | Fail |  | 60 |  |  |  | 1.8
| 61 | [14 empty] | Fail |  | 61 |  |  |  | 3.825
| 62 | [14 empty] | Fail |  | 62 |  |  |  | 18.822
| 63 | [14 empty] | Fail |  | 63 |  |  |  | 2.45
| 64 | [14 empty] | Fail |  | 64 |  |  |  | 0.613
| 65 | [14 empty] | Fail |  | 65 |  |  |  | 0.453
| 66 | [14 empty] | Fail |  | 66 |  |  |  | 1.074
| 67 | [14 empty] | Fail |  | 67 |  |  |  | 5.504
| 68 | [14 empty] | Fail |  | 68 |  |  |  | 1.967
| 69 | [14 empty] | Fail |  | 69 |  |  |  | 20.81
| 70 | [14 empty] | Fail |  | 70 |  |  |  | 1.018
| 71 | [14 empty] | Fail |  | 71 |  |  |  | 2.735
| 72 | [14 empty] | Fail |  | 72 |  |  |  | 12.761
| 73 | [5 empty] | Environment team - OFW-OBQ-UUW-030-UUW response.pdf - All Documents (sharepoint.com); Environment team - OFW-OBQ-UUW-052-UUW response.pdf - All Documents (sharepoint.com) | Ref 30: Query related to overlap with WINEP Ref 52: Clarificaiton of WINEP drivers and names of sites under the scheme | Ref: 30 Our net zero enhancement project, Process emissions (Bioresources) has a primary driver of GHG emissions reduction and funding has not been requested elsewhere and is not covered by any WINEP or Industrial Emissions Directive drivers. Ref 52: Provided in the query response | [6 empty] | Fail |  | 73 |  |  |  | 13.776
| 74 | NWT | E00001339 | Process emissions (Wastewater) | Process emissions | (UUW) Introduce innovative technologies to monitor and reduce the release of nitrous oxide from wastewater processes. Sector leading nitrous oxide (N2O) emissions reduction programme. (Interpretation from narrative is this is Real Time Control). Real Time Control includes the use of sensors and monitoring equipment including liquid and gas sensors. This monitoring is connected online monitoring and process control, such as adjusting air flow or ammonia-based aeration control (ABAC). The load can also be adjusted. This tends to require some infrastructure changes including adjustable nozzle upgrades for aeration blowers. | OFW-OBQ-UUW-120 - UUW response.pdf; Environment team - OFW-OBQ-UUW-041-UUW response.pdf - All Documents (sharepoint.com); Environment team - OFW-OBQ-UUW-110- UUW response (002).pdf - All Documents (sharepoint.com) | Ref 120: Request for clarification of the technologies proposed for deployment to mitigate N2O emissions. Ref 41: Clarification of cumulative benefits of Net Zero enhancement scheme Ref 110: To understand monitoring for the proposed schemes | Ref 120: Installation of one nitrate analyser per lane, installation of one ammonia analyser every two lanes and installation of real time control to integrate current and new analysers with the control system, to adjust dissolved oxygen (DO) and minimise nitrous oxide production Ref 41: Details of benefits provided in query response Ref 110: Details provided in query response | Real Time Control - Medium - TRL 7 - technology prototype demonstration in an operational environment | Real time control: developing technology, new technology for the sector and essential for N2O reductions | Real time control - Medium | Real time control: control of the process variables is expected to support reductions in emissions but can be offset by changes in energy demand for aeration to reduce N2O. | No | The scheme is driven by N2O mitigation and not affected by IED | Pass | Representations referenced digital integration, a threshold requirement for innovation, learning, and efficiency. Schemes meet the innovation threshold due to absence of schemes in the UK, and requirement for piloting. Monitoring is not standard practice in the industry, especially not with control. | 74 | NWT | E00001339 | Process emissions (Wastewater) | 34.104
| 75 | [14 empty] | Fail |  | 75 |  |  |  | 5.808
| 76 |  |  | Up to here for Query updates |  | Procuring zero emission (Electric Vehicle, EV) cars & vans | [9 empty] | Fail |  | 76 |  |  |  | 11.725
| 77 | [14 empty] | Fail |  | 77 |  |  |  | 1.224
| 78 | [14 empty] | Fail |  | 78 |  |  |  | 60.701
| 79 | [14 empty] | Fail |  | 79 |  |  |  | 2.411
| 80 | NWT | E00001425 | Net zero catchment strategy | NBS | Working with partners, UU wants to develop a sustainability masterplan and test innovative approaches ​for low carbon water and wastewater priorities in the major new development of St Cuthbert's Garden ​Village (10,000 houses over a 30y period). This could include working with developers on storing surface water, recycling grey water, exploring ways to protect the sewers in operation (such as making smarter design choices and increasing community engagement) and potential reuse of low-grade heat from the sewer network. Also include minimising the need at the treatment works (enhanced treatment solutions and local composting) and opportunities to re-use by products from the treatment process. Carbon benefits are uncertain since UU still has to decide on specific interventions. ​ | OFW-OBQ-UUW-041-UUW response.pdf | #41 To understand the carbon abatement impact of the scheme | “At this early stage it is not possible to accurately quantify the potential for emissions reductions, as it is dependent on the phasing of the St Cuthbert’s Garden Village development. This first phase of work is to explore this in detail with partners to develop a masterplan, vision and supporting policies. We do not expect this first phase to deliver reductions itself, but the work completed in early AMP8 will be the enabler to substantial future emissions reductions as the development commences, and those benefits would continue to be felt for the lifespan of the new community. We would also explore options to test and trial latest innovations that could deliver reductions in this phase, depending on potential and timing. This visionary project has the potential to inform improvements nationally for far wider benefits.” | Catchment Management - High | Innovative project to create a net zero community in the context of a large housing development. Catchment system at early stages of development with opportunity to focus on net zero technology, with emphasise on sector learning | Low | The scheme is at its very beginning and interventions are not clearly defined yet. The project would contribute to an integrated strategy for water with meaningful impact on the 2050 target of the UK. The project is very uncertain and will depend on the agreement reached with development partners. So it is not directly contextualised in their LTDS because benefits are not yet clearly identified. | NA |  | Pass | The scheme is clearly driven by net zero and enhancement. However, it is quite uncertain in terms of interventions and benefits. It would clearly contribute to sector learning by allowing UU to try new practices in sustainable water management. | 80 | NWT | E00001425 | Net zero catchment strategy | 1.016
| 81 | WSH | CWW22_1 | Net Zero Carbon Strategy: Network Control Systems (Wastewater) | Process emissions | Delivery of a new Network Control System for Wastewater to reduce energy consumption by using factors such as weather and demand patterns to predict optimum set points, and as a result, control and optimise pumping regimes | NA | [8 empty] | Fail |  | 81 |  |  |  | 1.304
| 82 | WSH | CWW22_2 | Net Zero Carbon Strategy: Reduction of Process Emissions | Process emissions | This enhanced investment case will deliver an advanced process control system to reduce N2O emissions and reduce energy consumption (enabled by investment in new blowers at 14 sites and new diffusers at 20 sites). Real Time Control - Use of sensors and monitoring equipment including liquid and gas sensors. This monitoring is connected online monitoring and process control, such as adjusting air flow or ammonia-based aeration control (ABAC). The load can also be adjusted. This tends to require some infrastructure changes such as new blowers and diffusers. | NA | [8 empty] | Pass |  | 82 | WSH | CWW22_2 | Net Zero Carbon Strategy: Reduction of Process Emissions | 35.866
| 83 | WSX | CWW22_1 | Heat recovery | Fossil fuel reduction | Heat recovery (Avo SBR effluent) - displacing fossil gas | [9 empty] | Fail | Base Uplift | 83 |  |  |  | -3.69
| 84 | WSX | CWW22_2 | Nitrous oxide - standard enhancement | Process emissions | Monitoring & control of N2O at 7 sites (out of total 20), under standard enhancement drivers. Use of sensors and monitoring equipment including liquid and gas sensors. This monitoring is connected online monitoring and process control, such as adjusting air flow or ammonia-based aeration control (ABAC). The load can also be adjusted. Controlling emissions tends to require some infrastructure changes such as adjustable blowers and diffusers. | OFW-OBQ-WSX-145-WSX response.docx (sharepoint.com) | Query to understand how the schemes will be monitored for results | Investigatory monitoring will take place for two years, with the default technology being sensors that measure N2O in solution in the aqueous phase. Two years of continuous monitoring will help us better understand the cause-effect relationships at specific sites of the variables noted above and N2O formation, while also allowing us to see the degree to which N2O spikes can be prevented and whether levels observed at other times can be reduced. After two years of monitoring at the first tranche of sites, rigs will be de-mounted, moved and re-assembled at other WRCs to repeat the exercise. | Low | This presents limited innovation in optimising assets. There is some learning to be taken from controlling the asset. [TRL 7 – Deployment] | High | There is research and literature to show this has impacts on the N2O emitted from wastewater sites | No | Solution is designed for the wastewater treatment stage prior to bioresources treatment | Pass | Representations referenced digital integration, a threshold requirement for innovation, learning, and efficiency. Schemes meet the innovation threshold due to absence of schemes in the UK, and requirement for piloting. Monitoring is not standard practice in the industry, especially not with control. | 84 | WSX | CWW22_2 | Nitrous oxide - standard enhancement | 0.852
| 85 | WSX | CWW22_3 | Nitrous oxide - NZ challenge | Process emissions | Monitoring & control, 13 sites (out of 20), net zero carbon challenge. Investigatory monitoring will take place for two years, with the default technology being sensors that measure N2O in solution in the aqueous phase. Two years of continuous monitoring will help us better understand the cause effect relationships at specific sites of the variables noted above and N2O formation, while also allowing us to see the degree to which N2O spikes can be prevented and whether levels observed at other times can be reduced. After two years of monitoring at the first tranche of sites, rigs will be de-mounted, moved and re-assembled at other WRCs to repeat the exercise. | OFW-OBQ-WSX-145-WSX response.docx (sharepoint.com) | Query to understand how the schemes will be monitored for results | Investigatory monitoring will take place for two years, with the default technology being sensors that measure N2O in solution in the aqueous phase. Two years of continuous monitoring will help us better understand the cause-effect relationships at specific sites of the variables noted above and N2O formation, while also allowing us to see the degree to which N2O spikes can be prevented and whether levels observed at other times can be reduced. After two years of monitoring at the first tranche of sites, rigs will be de-mounted, moved and re-assembled at other WRCs to repeat the exercise. | Process monitoring and optimisation for nitrous oxide reduction - TRL8 - actual technology completed and qualified through test and demonstration | Monitoring of N2O emissions is essential to setting a reliable baseline of emissions and then making interventions. The application of monitoring is still in development and there is currently no alternative deployment of soft sensor/digital approaches for montoring. Monitoring does not present a net zero technology for reducing emissions, but it does enable response to be implemented with the data it produces. | Process monitoring and optimisation for nitrous oxide reduction - Low | Monitoring to create a baseline of N2O emissions is essential for implementing responses for reduction of emissions, however it does not reduce emissions itself. | No | Solution is designed for the wastewater treatment stage prior to bioresources treatment | Pass | Representations referenced digital integration, a threshold requirement for innovation, learning, and efficiency. Schemes meet the innovation threshold due to absence of schemes in the UK, and requirement for piloting. Monitoring is not standard practice in the industry, especially not with control. | 85 | WSX | CWW22_3 | Nitrous oxide - NZ challenge | 1.37
| 86 | [14 empty] | Fail |  | 86 |  |  |  | 7.131
| 87 | [14 empty] | Fail |  | 87 |  |  |  | 3.9
| 88 | [14 empty] | Fail |  | 88 |  |  |  | 2.281
| 89 | [14 empty] | Fail |  | 89 |  |  |  | 10.796
| 90 | YKY | CWW22-2 | Methane reduction | Process emissions | Investment to reduce methane emissions from process via digester upgrade, vacuum degassing and leak detection | OFW-OBQ-YKY-040 - response.docx (sharepoint.com) | To understand the specific actions under the scheme | In summary, we have proposed three key activities related to methane reduction as follows: Upgrading of digesters to in-series configuration at 3 wastewater treatment sites (Blackburn Meadows, Esholt and Dewsbury). This improves digestion and importantly increases biogas yield and reduces downstream methane emissions. Vacuum degassing post-digester to remove further methane entrained in the digestate at 9 sites (the 3 indicated in A, plus Knostrop, Huddersfield, Hull, Woodhouse Mill, Old Whittington and Sandall). Methane leak detection across the 9 sites (as identified in A and B) to identify leaks from digesters, pipes, valves, flanges etc., to target repair and maintenance. | Vacuum Degassing - TRL 7 - technology prototype demonstration in an operational environment Series digester - medium | Vacuum degassing: It is considered a newer technology but is unlikely to fulfil requirements for innovation. Trials completed in period 2020-2025. Vacuum degassing - is a pump attached to a tank which withdraws gas from the sewage sludge reducing the residual emissions in the sludge and increasing its density. Commercial systems are relatively new. The magnitude of methane emissions reduction, net of the energy requirement to run the system, remains to be published by commercial vendors who to date claim that the increased biogas yield through system installation is sufficient for operation of the plant and equipment. It remains to be seen how big an impact vacuum extraction will have on methane emissions as a component of wider proactive methane mitigation measures and its cost effectiveness. Series digesters: Few existing schemes in 2020-2025. Reduction in redundancy and potentially efficiency as a result minimised time for maintenance | Vacuum degassing - medium Series digester - medium | Vacuum degassing: newer technology with a simple process Series digester: the process involves relatively simple engineering to re-plum the digester Monitoring: monitoring methane will not reduce emissions itself but present data regarding fugitive emissions | Yes | Ofwat's view is that anything dealing with pollutants from bioresources is an IED driver. Yorkshire Water's view (Query 40) is: The investment being undertaken in period 2020-2025 is for IED compliance, or that proposed as part of our Appropriate Measures Enhancement case YKY42 Appropriate measures enhancement case for 2025-2030 does not relate to the Net zero investment being made. The vacuum degassing installations proposed under Net Zero enhancement are designed to remove methane from the post digested sludge. Yorkshire Water has no plans to cover our post digested sludge storage tanks under IED for the purposes of capturing methane and has demonstrated through testing that it is not required. If covers are required on these tanks under IED or Appropriate Measures, the driver will be odour management, which could require a tank cover and odour control unit. However, any such odour control unit would not be designed to remove methane which is an odourless gas. | Pass | Vacuum degassing removes methane from sludge as it leaves the digester. The IED affects only the capture of methane from tanks. VD can demonstrate innovation and is expected to be revenue neutral. Series digester upgrades will likely help with redundancy and operation of the asset. This is a base cost | 90 | YKY | CWW22-2 | Methane reduction | 19.38
| 91 | YKY | CWW22-3 | Nitrous oxide reduction | Process emissions | Use of sensors and monitoring equipment including liquid and gas sensors. This monitoring is connected online monitoring and process control, such as adjusting air flow or ammonia-based aeration control (ABAC). The load can also be adjusted. This tends to require some infrastructure changes. Investment to reduce nitrous oxide emissions from ASP lanes via use of real time control coupled with monitoring of emission and limited additional investment in liquor buffering. | OFW-OBQ-YKY-130 - response.docx (sharepoint.com) | To understand further details of how the scheme will be monitored | For CWW22-3 we have included both capex and opex for monitoring of the effectiveness of our proposed nitrous oxide reduction investments. This provides for baseline and on-going monitoring at all sites where we make investment and is indicated as intervention 0 in Table 1.14 (mis-labelled as 1.1413) in our enhancement case. An indication of the site capex and opex allocated is shown in Figure 1.2, so we have included a significant investment across all sites. We have included monitoring costs for nitrous oxide monitoring using multiple Unisense monitors as recognised as the best means to measure emissions on a real time basis across ASP lanes and establish emission factors to enable emissions to be determined. We have allowed c. £28.5K capex and an annual c. £57k opex for each of the 13 sites with proposed nitrous oxide reductions aligned to the phased implementation of interventions. As part of our review of monitoring costs we will check that the amounts allocated are sufficient to facilitate monitoring at each site, and cover baseline investigations. It is envisaged that reporting will be integrated into APR reporting related to the performance commitments. | Real Time Control - Medium - TRL 7 - technology prototype demonstration in an operational environment Process monitoring and optimisation for nitrous oxide reduction - TRL8 - actual technology completed and qualified through test and demonstration | Real time control: developing technology, new technology for the sector and essential for N2O reductions Monitoring of N2O emissions is essential to setting a reliable baseline of emissions and then making interventions. The application of monitoring is still in development and there is currently no alternative deployment of soft sensor/digital approaches for montoring. Monitoring does not present a net zero technology for reducing emissions, but it does enable response to be implemented with the data it produces. | Real time control - Medium Process monitoring and optimisation for nitrous oxide reduction - Low | Vacuum degassing: is a technical solution which, while there is no current data, would still be expected to capture methane. The net emisisons of running the vacuum chamber are not certain. Real time control: control of the process variables is expected to support reductions in emissions but can be offset by changes in energy demand for aeration to reduce N2O. Monitoring to create a baseline of N2O emissions is essential for implementing responses for reduction of emissions, however it does not reduce emissions itself. | No | Solution is designed for the wastewater treatment stage prior to bioresources treatment | Pass | Representations referenced digital integration, a threshold requirement for innovation, learning, and efficiency. Schemes meet the innovation threshold due to absence of schemes in the UK, and requirement for piloting. Monitoring is not standard practice in the industry, especially not with control. | 91 | YKY | CWW22-3 | Nitrous oxide reduction | 12.574
|  |  | Totex (£m) | 528.57 | [15 empty] | Totex (£m) | 467.2131
|  |  | AMP8 benefits (tCO2e) | -335861.971 | [15 empty] | AMP8 benefits (tCO2e) | -318796.371
Process description Schemes which passed Phase 1 were assessed at Phase 2. References to the scheme including queries issued to the proposing company were catalogued. The key aspects of this phase were to: - review the technology maturity and contribution to innovation, sector learning and efficiency. - assess confidence of the delivery of emissions abatement - further review where a scheme is affected or driven by the Industrial Emissions Directive Additional expert opinion was sought in the instances where it was difficult to judge the technical merits, cost, commercial opportunities, or level of innovation of a scheme. Three rounds of expert review were provided: 1. Review of schemes with Richard Chamley, PR24 Engineering Advisor (18/12/23) 2. Review of schemes with Edoard Piano, PR24 Engineering Advisor (20/12/23) 3. Review of schemes with Eugenia Vela, Senior Associate, Water Engineer (29/1/24) Overview of decisions Decisions related to technology maturity and contribution to innovation, sector learning and efficiency were driven by the following considerations: - technology maturity should be sufficient to give confidence that it can be delivered and offer value for money for customers, however it should not be so mature that it is using existing technology which is commonplace in the sector to the extent it would form part of general maintenance and operation of an asset. - innovation and sector learning is demonstrated by alternative or newer technologies which are not yet commonplace in the wastewater sector but offer confidence that they might deliver emissions reductions - efficiency was deemed to have been met where the technology proposed offered a step change to a new model of operation. The Industrial Emissions Directive (IED) has been important for the assessment of schemes. Where the IED is a driver a scheme is ineligible for Net Zero Enhancement. Where Net Zero and emissions abatement are a driver but there are commercial benefits attached to the scheme, the scheme has not passed. This is particularly relevant for schemes which optimise the general operation of an asset or create a revenue stream (e.g. increase collection of biogas and biomethane for reuse). Net Zero as a primary driver for a scheme is expected to show emissions abatement through applying a technology soley for that purpose.

## Unit Costs
#VALUE!
| Scheme submitted |  |  |  | Carbon benefits | [9 empty] | Stated asset life
|  | Company | Scheme ID | Scheme name | AMP8 totex (£m) | BPT stated carbon benefits (tCO2e) | AMP8 (£000/tCO2e) | AMP8 £/tCO2e | 5 years £/tCO2e | 10 years £/tCO2e | 15 years £/tCO2e | 20 years £/tCO2e | 25 years £/tCO2e | 30 years £/tCO2e | Years | tCo2e
| 1 | ANH | CWW22.1 | Cotton Valley STC - Centrate quality | 14.6275 | -287.5 | 50.8783 | 50878.3091 | 10175.6618 | 5087.8309 | 3391.8873 | 2543.9155 | 2035.1324 | 1695.9436 |  | 4155.0619
2
3
4
5
6
7
8
9
10
11
12
13
| 14 | ANH | CWW22.14 | Basildon STC Fugitive emissions N2O | 1.5555 | -174 | 8.9395 | 8939.4998 | 1787.9 | 893.95 | 595.9667 | 446.975 | 357.58 | 297.9833 |  | 730.0591
| 15 | ANH | CWW22.15 | Colchester STC Fugitive emissions N2O | 1.4711 | -580 | 2.5364 | 2536.4313 | 507.2863 | 253.6431 | 169.0954 | 126.8216 | 101.4573 | 84.5477 |  | 207.1419
| 16 | ANH | CWW22.16 | Cliff Quay STC Fugitive emissions N2O | 1.6 | -273 | 5.8609 | 5860.9263 | 1172.1853 | 586.0926 | 390.7284 | 293.0463 | 234.4371 | 195.3642 |  | 478.6423
17
| 18 | ANH | CWW22.18 | Cotton Valley WRC Fugitive emissions N2O | 1.7013 | -885.417 | 1.9215 | 1921.5 | 384.3 | 192.15 | 128.1 | 96.075 | 76.86 | 64.05 |  | 156.9225
| 19 | ANH | CWW22.19 | Great Billing WRC Fugitive Emissions N2O | 2.0673 | -450.45 | 4.5895 | 4589.5097 | 917.9019 | 458.951 | 305.9673 | 229.4755 | 183.5804 | 152.9837 |  | 374.81
| 20 | ANH | CWW22.20 | Basildon WRC Fugitive Emissions N2O | 1.7611 | -214.25 | 8.2196 | 8219.613 | 1643.9226 | 821.9613 | 547.9742 | 410.9807 | 328.7845 | 273.9871 |  | 671.2684
| 21 | ANH | CWW22.21 | Bedford WRC Fugitive Emissions N2O | 0.74849 | -315.25 | 2.3743 | 2374.2627 | 474.8525 | 237.4263 | 158.2842 | 118.7131 | 94.9705 | 79.1421 |  | 193.8981
| 22 | ANH | CWW22.22 | Kings Lynn WRC Fugitive Emissions N2O | 0.95194 | -221.5 | 4.2977 | 4297.7103 | 859.5421 | 429.771 | 286.514 | 214.8855 | 171.9084 | 143.257 |  | 350.9797
| 23 | ANH | CWW22.23 | Newton Marsh WRC Fugitive Emissions N2O | 0.4468 | -72.5 | 6.1628 | 6162.7945 | 1232.5589 | 616.2794 | 410.853 | 308.1397 | 246.5118 | 205.4265 |  | 503.2949
| 24 | ANH | CWW22.24 | Broadholme WRC Fugitive Emissions N2O | 0.64794 | -260.208 | 2.4901 | 2490.0776 | 498.0155 | 249.0078 | 166.0052 | 124.5039 | 99.6031 | 83.0026 |  | 203.3563
| 25 | ANH | CWW22.25 | Letchworth WRC Fugitive emissions N2O | 11.3471 | -127.6 | 88.9268 | 88926.7971 | 17785.3594 | 8892.6797 | 5928.4531 | 4446.3399 | 3557.0719 | 2964.2266 |  | 7262.3551
| 26 | ANH | CWW22.26 | Newmarket WRC Fugitive Emissions N2O | 4.6082 | -26.5 | 173.8945 | 173894.5494 | 34778.9099 | 17389.4549 | 11592.97 | 8694.7275 | 6955.782 | 5796.485 |  | 14201.3882
| 27 | ANH | CWW22.27 | Hitchin WRC Fugitive emissions N2O | 0.7844 | -32.95 | 23.8057 | 23805.7311 | 4761.1462 | 2380.5731 | 1587.0487 | 1190.2866 | 952.2292 | 793.5244 |  | 1944.1347
| 28 | ANH | CWW22.28 | Dunstable WRC Fugitive Emissions N2O | 12.274 | -75.3 | 163.0011 | 163001.1076 | 32600.2215 | 16300.1108 | 10866.7405 | 8150.0554 | 6520.0443 | 5433.3703 |  | 13311.7571
| 29 | ANH | CWW22.29 | Flitwick WRC Fugitive Emissions N2O | 6.4209 | -139.514 | 46.0234 | 46023.4063 | 9204.6813 | 4602.3406 | 3068.2271 | 2301.1703 | 1840.9363 | 1534.1135 |  | 3758.5782
30
31
32
33
34
35
| 36 | ANH | CWW22.36 | Huntingdon WRC Fugitive Emissions N2O | 0.53303 | -60.2 | 8.8543 | 8854.2678 | 1770.8536 | 885.4268 | 590.2845 | 442.7134 | 354.1707 | 295.1423 |  | 723.0985
37
38
39
40
41
42
43
44
| 45 | ANH | CWW22.45 | Colchester WRC Fugitive Emissions N2O | 11.958 | -286.758 | 41.7007 | 41700.6675 | 8340.1335 | 4170.0667 | 2780.0445 | 2085.0334 | 1668.0267 | 1390.0222 |  | 3405.5545
| 46 | HDD | CWW22.1 | Process Emissions Reduction | 0.86355 | -411.398 | 2.0991 | 2099.0622 | 419.8124 | 209.9062 | 139.9375 | 104.9531 | 83.9625 | 69.9687 |  | 171.4234
47
| 48 | SVE | NZ#1 | Digital Twin | 53.341 | -8600 | 6.2024 | 6202.4419 | 1240.4884 | 620.2442 | 413.4961 | 310.1221 | 248.0977 | 206.7481 | 30 | 506.5328
| 49 | SVE | NZ#2 | Cover & Treat | 92.895 | -74239.11 | 1.2513 | 1251.2946 | 250.2589 | 125.1295 | 83.4196 | 62.5647 | 50.0518 | 41.7098 | 30 | 102.1891
| 50 | SVE | NZ#3 | ASP Intensification | 104.111 | -49959.36 | 2.0839 | 2083.9138 | 416.7828 | 208.3914 | 138.9276 | 104.1957 | 83.3566 | 69.4638 | 30 | 170.1863
| 51 | SVE | NZ#4 | Active gas capture | 35.621 | -13593 | 2.6205 | 2620.54 | 524.108 | 262.054 | 174.7027 | 131.027 | 104.8216 | 87.3513 | 30 | 214.0108
52
53
54
| 55 | SVE |  | Cellulose recovery
| 56 | SVE | NZ#9 | Process Optimisation | 8.967 | -24600 | 0.36451 | 364.5122 | 72.9024 | 36.4512 | 24.3008 | 18.2256 | 14.5805 | 12.1504 | 30 | 29.7685
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
| 74 | NWT | E00001339 | Process emissions (Wastewater) | 34.1044 | -62705.206 | 0.54388 | 543.8848 | 108.777 | 54.3885 | 36.259 | 27.1942 | 21.7554 | 18.1295 | 28 | 44.4173
75
76
77
78
79
| 80 | NWT | E00001425 | Net zero catchment strategy | 1.0164 | 0 | -
| 81 | WSH |  | Net Zero Carbon Strategy: Network Control Systems (Wastewater)
| 82 | WSH | CWW22_2 | Net Zero Carbon Strategy: Reduction of Process Emissions | 35.358 | -19372 | 1.8252 | 1825.2094 | 365.0419 | 182.5209 | 121.6806 | 91.2605 | 73.0084 | 60.8403 |  | 149.0588
| 83 | WSX |  | Heat recovery
| 84 | WSX | CWW22_2 | Nitrous oxide - standard enhancement | 0.85153 | -1978 | 0.4305 | 430.5029 | 86.1006 | 43.0503 | 28.7002 | 21.5251 | 17.2201 | 14.3501 |  | 35.1577
| 85 | WSX | CWW22_3 | Nitrous oxide - NZ challenge | 1.3695 | -892.4 | 1.5347 | 1534.6787 | 306.9357 | 153.4679 | 102.3119 | 76.7339 | 61.3871 | 51.156 |  | 125.3321
86
87
88
89
| 90 | YKY | CWW22-2 | Methane reduction | 10.009 | -41709 | 0.23997 | 239.9722 | 47.9944 | 23.9972 | 15.9981 | 11.9986 | 9.5989 | 7.9991 |  | 19.5977
| 91 | YKY | CWW22-3 | Nitrous oxide reduction | 13.201 | -16254 | 0.81217 | 812.1693 | 162.4339 | 81.2169 | 54.1446 | 40.6085 | 32.4868 | 27.0723 |  | 66.3272
Process description The schemes were assessed against the unit cost of abatement (£/tCO2e abated). For the unit cost of abatement, the schemes were assessed using the information available for AMP 8 - the value of the investment in AMP 8 and emissions abated in AMP 8. However, this did not produce unit costs of abatement comparable to government values for unit costs of abatement under the UK Govenments valuation of greenhouse gas emissions, 2021 (https://www.gov.uk/government/publications/valuing-greenhouse-gas-emissions-in-policy-appraisal/valuation-of-greenhouse-gas-emissions-for-policy-appraisal-and-evaluation). Scheme costs were extrapolated across a 20 year period to reflect a more realistic asset life of investments where no further information was provided by companies. Where companies have calculated the unit cost of abatement this has been recorded.

## Phase 3 - Unit Cost Ranking
#VALUE!
| Schemes passed in phase 2 |  |  |  | Unit costs |  | Phase 3 decisions
|  | Company | Scheme ID | Scheme name | Unit cost over AMP8 (£/tCO2e) | Unit cost over 20 years (£/tCO2e) | Phase 3 decision | Justification
| 1 | ANH | CWW22.1 | Cotton Valley STC - Centrate quality | 50878.3091 | 2543.9155 | Pass | Decision was made not to take out schemes based on unit costs
| 2 | ANH | CWW22.14 | Basildon STC Fugitive emissions N2O | 8939.4998 | 446.975 | Pass | Decision was made not to take out schemes based on unit costs
| 3 | ANH | CWW22.15 | Colchester STC Fugitive emissions N2O | 2536.4313 | 126.8216 | Pass | Decision was made not to take out schemes based on unit costs
| 4 | ANH | CWW22.16 | Cliff Quay STC Fugitive emissions N2O | 5860.9263 | 293.0463 | Pass | Decision was made not to take out schemes based on unit costs
| 5 | ANH | CWW22.18 | Cotton Valley WRC Fugitive emissions N2O | 1921.5 | 96.075 | Pass | Decision was made not to take out schemes based on unit costs
| 6 | ANH | CWW22.19 | Great Billing WRC Fugitive Emissions N2O | 4589.5097 | 229.4755 | Pass | Decision was made not to take out schemes based on unit costs
| 7 | ANH | CWW22.20 | Basildon WRC Fugitive Emissions N2O | 8219.613 | 410.9807 | Pass | Decision was made not to take out schemes based on unit costs
| 8 | ANH | CWW22.21 | Bedford WRC Fugitive Emissions N2O | 2374.2627 | 118.7131 | Pass | Decision was made not to take out schemes based on unit costs
| 9 | ANH | CWW22.22 | Kings Lynn WRC Fugitive Emissions N2O | 4297.7103 | 214.8855 | Pass | Decision was made not to take out schemes based on unit costs
| 10 | ANH | CWW22.23 | Newton Marsh WRC Fugitive Emissions N2O | 6162.7945 | 308.1397 | Pass | Decision was made not to take out schemes based on unit costs
| 11 | ANH | CWW22.24 | Broadholme WRC Fugitive Emissions N2O | 2490.0776 | 124.5039 | Pass | Decision was made not to take out schemes based on unit costs
| 12 | ANH | CWW22.25 | Letchworth WRC Fugitive emissions N2O | 88926.7971 | 4446.3399 | Pass | Decision was made not to take out schemes based on unit costs
| 13 | ANH | CWW22.26 | Newmarket WRC Fugitive Emissions N2O | 173894.5494 | 8694.7275 | Pass | Decision was made not to take out schemes based on unit costs
| 14 | ANH | CWW22.27 | Hitchin WRC Fugitive emissions N2O | 23805.7311 | 1190.2866 | Pass | Decision was made not to take out schemes based on unit costs
| 15 | ANH | CWW22.28 | Dunstable WRC Fugitive Emissions N2O | 163001.1076 | 8150.0554 | Pass | Decision was made not to take out schemes based on unit costs
| 16 | ANH | CWW22.29 | Flitwick WRC Fugitive Emissions N2O | 46023.4063 | 2301.1703 | Pass | Decision was made not to take out schemes based on unit costs
| 17 | ANH | CWW22.36 | Huntingdon WRC Fugitive Emissions N2O | 8854.2678 | 442.7134 | Pass | Decision was made not to take out schemes based on unit costs
| 18 | ANH | CWW22.45 | Colchester WRC Fugitive Emissions N2O | 41700.6675 | 2085.0334 | Pass | Decision was made not to take out schemes based on unit costs
| 19 | HDD | CWW22.1 | Process Emissions Reduction | 2099.0622 | 104.9531 | Pass | Decision was made not to take out schemes based on unit costs
| 20 | SVE | NZ#1 | Digital Twin | 6202.4419 | 310.1221 | Pass | Decision was made not to take out schemes based on unit costs
| 21 | SVE | NZ#2 | Cover & Treat | 1251.2946 | 62.5647 | Pass | Decision was made not to take out schemes based on unit costs
| 22 | SVE | NZ#3 | ASP Intensification | 2083.9138 | 104.1957 | Pass | Decision was made not to take out schemes based on unit costs
| 23 | SVE | NZ#4 | Active gas capture | 2620.54 | 131.027 | Pass | Decision was made not to take out schemes based on unit costs
| 24 | SVE | NZ#9 | Process Optimisation | 364.5122 | 18.2256 | Pass | Decision was made not to take out schemes based on unit costs
| 25 | NWT | E00001339 | Process emissions (Wastewater) | 543.8848 | 27.1942 | Pass | Decision was made not to take out schemes based on unit costs
| 26 | NWT | E00001340 | Process emissions (Wastewater) | 468.7707 | - | Pass | Decision was made not to take out schemes based on unit costs
| 27 | WSH | CWW22_2 | Net Zero Carbon Strategy: Reduction of Process Emissions | 1825.2094 | 91.2605 | Pass | Decision was made not to take out schemes based on unit costs
| 28 | WSX | CWW22_2 | Nitrous oxide - standard enhancement | 430.5029 | 21.5251 | Pass | Decision was made not to take out schemes based on unit costs
| 29 | WSX | CWW22_3 | Nitrous oxide - NZ challenge | 1534.6787 | 76.7339 | Pass | Decision was made not to take out schemes based on unit costs
| 30 | YKY | CWW22-2 | Methane reduction | 239.9722 | 11.9986 | Pass | Decision was made not to take out schemes based on unit costs
| 31 | YKY | CWW22-3 | Nitrous oxide reduction | 812.1693 | 40.6085 | Pass | Decision was made not to take out schemes based on unit costs
Process description Phase three drew from the deep dive review of process emissions schemes. It identifies where, according to the limited unit cost of abatement benchmarking, schemes showed best value for emissions abatement.

## Allowance
Allowance
Summary of allowed costs
| Final list of schemes | [5 empty] | AMP8 totex (£m) | [6 empty] | Cumulated carbon benefits (tCO2e)
|  | Company | Scheme ID | Scheme name | Selected or Feasible |  | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | AMP8 totex |  | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | AMP8 benefits
| 1 | ANH | CWW22.1 | Cotton Valley STC - Centrate quality | Selected |  | 0 | 0.48865 | 3.4843 | 6.126 | 4.5286 | 14.6275 |  | 0 | 0 | 0 | 0 | -287.5 | -287.5
| 2 | ANH | CWW22.14 | Basildon STC Fugitive emissions N2O | Selected |  | 0 | 0 | 0.30472 | 0.71523 | 0.53552 | 1.5555 |  | 0 | 0 | 0 | 0 | -174 | -174
| 3 | ANH | CWW22.15 | Colchester STC Fugitive emissions N2O | Selected |  | 0.28658 | 0.57316 | 0.5807 | 0.010084 | 0.020609 | 1.4711 |  | 0 | 0 | -116 | -348 | -580 | -580
| 4 | ANH | CWW22.16 | Cliff Quay STC Fugitive emissions N2O | Selected |  | 0 | 0 | 0.31847 | 0.63695 | 0.64461 | 1.6 |  | 0 | 0 | 0 | 0 | -273 | -273
| 5 | ANH | CWW22.18 | Cotton Valley WRC Fugitive Emissions N20 | Selected |  | 0.34027 | 0.68053 | 0.68053 | 0 | 0 | 1.7013 |  | 0 | 0 | -35.417 | -460.417 | -885.417 | -885.417
| 6 | ANH | CWW22.19 | Great Billing WRC Fugitive Emissions N20 | Selected |  | 0 | 0.41339 | 0.82677 | 0.82692 | 0.000274 | 2.0673 |  | 0 | 0 | 0 | -34.65 | -450.45 | -450.45
| 7 | ANH | CWW22.20 | Basildon WRC Fugitive emissions N2O | Selected |  | 0 | 0.12178 | 0.49044 | 0.74134 | 0.40749 | 1.7611 |  | 0 | 0 | 0 | -42.85 | -214.25 | -214.25
| 8 | ANH | CWW22.21 | Bedford WRC Fugitive Emissions N20 | Selected |  | 0 | 0.03742 | 0.1871 | 0.29938 | 0.22459 | 0.74849 |  | 0 | 0 | 0 | -63.05 | -315.25 | -315.25
| 9 | ANH | CWW22.22 | Kings Lynn WRC Fugitive Emissions N20 | Selected |  | 0.19039 | 0.38078 | 0.38078 | 0 | 0 | 0.95194 |  | 0 | 0 | -44.3 | -132.9 | -221.5 | -221.5
| 10 | ANH | CWW22.23 | Newton Marsh WRC Fugitive Emissions N20 | Selected |  | 0 | 0 | 0.089361 | 0.17872 | 0.17872 | 0.4468 |  | 0 | 0 | 0 | 0 | -72.5 | -72.5
| 11 | ANH | CWW22.24 | Broadholme wrc Fugitive Emissions N20 | Selected |  | 0.16084 | 0.28268 | 0.20442 | 0 | 0 | 0.64794 |  | 0 | 0 | -10.408 | -135.308 | -260.208 | -260.208
| 12 | ANH | CWW22.25 | Letchworth WRC Fugitive emissions N2O | Selected |  | 0 | 0.88886 | 2.5194 | 4.586 | 3.3527 | 11.3471 |  | 0 | 0 | 0 | 0 | -127.6 | -127.6
| 13 | ANH | CWW22.26 | Newmarket WRC Fugitive Emissions N2O | Selected |  | 0 | 0 | 0.91948 | 1.839 | 1.8498 | 4.6082 |  | 0 | 0 | 0 | 0 | -26.5 | -26.5
| 14 | ANH | CWW22.27 | Hitchin WRC Fugitive Emissions N20 | Selected |  | 0 | 0.052293 | 0.20917 | 0.31376 | 0.20917 | 0.7844 |  | 0 | 0 | 0 | -12.675 | -63.375 | -32.95
| 15 | ANH | CWW22.28 | Dunstable WRC Fugitive Emissions N2O | Selected |  | 0 | 0.95962 | 2.72 | 4.9511 | 3.6432 | 12.274 |  | 0 | 0 | 0 | 0 | -75.3 | -75.3
| 16 | ANH | CWW22.29 | Flitwick WRC Fugitive Emissions N2O | Selected |  | 0.52737 | 1.4682 | 2.5719 | 1.7562 | 0.097275 | 6.4209 |  | 0 | 0 | -3.532 | -51.214 | -139.514 | -139.514
| 17 | ANH | CWW22.36 | Huntingdon WRC Fugitive Emissions N20 | Selected |  | 0 | 0 | 0 | 0.17376 | 0.35927 | 0.53303 |  | 0 | 0 | 0 | 0 | -60.2 | -60.2
| 18 | ANH | CWW22.45 | Colchester WRC Fugitive Emissions N2O | Feasible |  | 0.93235 | 2.6427 | 4.8104 | 3.531 | 0.041357 | 11.958 |  | 0 | 0 | -264.7 | -22.058 | -286.758 | -286.758
| 19 | HDD | CWW22.1 | Process Emissions Reduction | Selected |  | 0.49147 | 0.29561 | 0.025488 | 0.025488 | 0.025488 | 0.86355 |  | 0 | 0 | -137.13 | -274.265 | -411.3975 | -411.398
| 20 | SVE | NZ#1 | Digital Twin | Selected |  | 12.786 | 25.571 | -2.118 | 8.551 | 8.551 | 53.341 |  | 0 | 0 | -1400 | -4300 | -8600 | -8600
| 21 | SVE | NZ#2 | Cover & Treat | Selected |  | 18.579 | 18.579 | 18.579 | 18.579 | 18.579 | 92.895 |  | 0 | 0 | -7607.71 | -23251.86 | -74239.11 | -74239.11
| 22 | SVE | NZ#3 | ASP Intensification | Selected |  | 4.076 | 28.561 | 25.891 | 23.954 | 21.629 | 104.111 |  | 0 | 0 | -8326.56 | -24979.68 | -49959.36 | -49959.36
| 23 | SVE | NZ#4 | Active gas capture | Selected |  | 0 | 0 | 12.948 | 8.714 | 13.959 | 35.621 |  | 0 | 0 | -1359 | -4078 | -8156 | -13593
| 24 | SVE | NZ#9 | Process Optimisation | Selected |  | 6.045 | 0 | 0.738 | 1.092 | 1.092 | 8.967 |  | 0 | 0 | -8200 | -16400 | -24600 | -24600
| 25 | NWT | E00001339 | Process emissions (wastewater) | Selected |  | 27.2204 | 1.6984 | 1.7133 | 1.7119 | 1.7604 | 34.1044 |  | 0 | 0 | -12541.041 | -37623.123 | -62705.206 | -62705.206
| 26 | NWT | E00001425 | Net zero catchment strategy | Selected |  | 0.50404 | 0.25636 | 0.15266 | 0.10336 | 0 | 1.0164 |  | 0 | 0 | 0 | 0 | 0 | 0
| 27 | WSH | CWW22_2 | Net Zero Carbon Strategy: Reduction of Process Emissions | Selected |  | 6.3079 | 7.2758 | 7.2641 | 7.3845 | 7.1256 | 35.358 |  | -10045 | -13831.5 | -16453 | -18157 | -19372 | -19372
| 28 | WSX | CWW22_2 | Nitrous oxide - standard enhancement | Selected |  | 0 | 0 | 0.61354 | 0.1187 | 0.11929 | 0.85153 |  | 0 | 0 | -652.74 | -1305.5 | -1978 | -1978
| 29 | WSX | CWW22_3 | Nitrous oxide- NZ challenge | Selected |  | 0.74424 | 0.11752 | 0.29789 | 0.10469 | 0.10521 | 1.3695 |  | 0 | 0 | -294.492 | -589 | -892.4 | -892.4
| 30 | YKY | CWW22-2 | Methane Reduction | Selected |  | 3.287 | 6.168 | 0.185 | 0.185 | 0.184 | 10.009 |  | 0 | -5397 | -19300 | -27806 | -41709 | -41709
| 31 | YKY | CWW22-3 | Nitrous oxide reduction | Selected |  | 5.693 | 3.875 | 1.211 | 1.211 | 1.211 | 13.201 |  | 0 | -2500 | -7000 | -9918 | -16254 | -16254
| Allowances per company in DD representations |  | AMP8 totex (£m) | [6 empty] | Cumulated carbon benefits (tCO2e) in DD representations | [6 empty] | Assessed totex (£m) in DD representations- Selected schemes |  |  | Assessed totex (£m) in DD representations- Feasible schemes |  | Assessed totex (£m) in DD representations- Selected and Feasible schemes
|  | Company | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | AMP8 totex |  | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | AMP8 benefits |  | Overall assessed totex | Company |  | Overall assessed totex | Company | Overall assessed totex | Company | Compared to CWW3
| 1 | ANH | 2.4378 | 8.99 | 21.298 | 26.6855 | 16.0932 | 75.5046 |  | 0 | 0 | -474.357 | -1303.122 | -4513.322 | -4482.897 |  | 64.2478 | ANH |  | 11.958 | ANH | 76.2058 | ANH | match
| 2 | HDD | 0.49147 | 0.29561 | 0.025488 | 0.025488 | 0.025488 | 0.86355 |  | 0 | 0 | -137.13 | -274.265 | -411.3975 | -411.398 |  | 0.86355 | HDD |  | 0 | HDD | 0.86355 | HDD | match
| 3 | NES | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | NES |  | 0 | NES | 0 | NES
| 4 | SVE | 41.486 | 72.711 | 56.038 | 60.89 | 63.81 | 294.935 |  | 0 | 0 | -26893.27 | -73009.54 | -165554.47 | -170991.47 |  | 365.359 | SVE |  | 14.232 | SVE | 379.591 | SVE | 415.133, checked CWW22 and the amount is 435.25
| 5 | SBB | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | SBB |  | 0 | SBB | 0 | SBB
| 6 | SRN | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | SRN |  | 0 | SRN | 0 | SRN
| 7 | TMS | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | TMS |  | 55.446 | TMS | 55.446 | TMS | 0, checked CWW22 and the amount is 55.45
| 8 | NWT | 27.7245 | 1.9547 | 1.8659 | 1.8153 | 1.7604 | 35.1208 |  | 0 | 0 | -12541.041 | -37623.123 | -62705.206 | -62705.206 |  | 42.1527 | NWT |  | 0 | NWT | 42.1527 | NWT | match
| 9 | WSH | 6.3079 | 7.2758 | 7.2641 | 7.3845 | 7.1256 | 35.358 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 36.6287 | WSH |  | 0 | WSH | 36.6287 | WSH | match
| 10 | WSX | 0.74424 | 0.11752 | 0.91143 | 0.22339 | 0.2245 | 2.2211 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 5.6616 | WSX |  | 6.1813 | WSX | 11.8429 | WSX | 5.66, seems that only selected schemes are counted
| 11 | YKY | 8.98 | 10.043 | 1.396 | 1.396 | 1.395 | 23.21 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 23.21 | YKY |  | 0 | YKY | 23.21 | YKY | match
| 12 | SWB | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | SWB |  | 0 | SWB | 0 | SWB
|  | Total | 88.1719 | 101.3877 | 88.7989 | 98.4201 | 90.4342 | 467.2131 |  | 0 | 0 | -40045.798 | -112210.05 | -233184.3955 | -238590.971 |  | 538.1234 |  |  | 87.8173 |  | 625.9407
Allowance requested in DD representations
Pivot Table Note: Select "scheme name" in pivot table options to see all schemes
| Sum of AMP8 totex (£m, 2025-30) | Column Labels
|  | Feasible |  | Feasible Total | Selected |  | Selected Total | Grand Total
| Row Labels | Fail | Pass |  | Fail | Pass
| ANH | 0 | 11.958 | 11.958 | 0.70116 | 63.5466 | 64.2478 | 76.2058
| HDD |  |  |  | 0 | 0.86355 | 0.86355 | 0.86355
| SVE | 14.232 |  | 14.232 | 70.424 | 350.593 | 421.017 | 435.249
| TMS | 55.446 |  | 55.446 |  |  |  | 55.446
| WSH |  |  |  | 1.2707 | 35.358 | 36.6287 | 36.6287
| WSX | 6.1813 |  | 6.1813 | 3.4406 | 2.2211 | 5.6616 | 11.8429
| YKY |  |  |  | 0 | 23.21 | 23.21 | 23.21
| NWT2 |  |  |  | 7.0319 | 35.1208 | 42.1527 | 42.1527
| Grand Total | 75.8593 | 11.958 | 87.8173 | 82.8683 | 510.9131 | 593.7814 | 681.5987

## F_Outputs
PR24CA88
Acronym | Reference | Item description | Unit | Model | Constant | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30
ANH | C_PR24CA88_ENH_WW_TOT | Total enhancement allowance - Wastewater - Net zero wastewater - Totex | £m | Price Review 2024 |  |  |  | 2.4378 | 8.99 | 21.298 | 26.6855 | 16.0932
ANH | C_PR24CA88_ENH_WW_AP | Total enhancement allowance - Wastewater - Net zero wastewater - Accelerated programme | £m | Price Review 2024
ANH | C_PR24CA88_ENH_WW_TE | Total enhancement allowance - Wastewater - Net zero wastewater - Transition allowance | £m | Price Review 2024
ANH | PR24QA_PR24CA88_OUT1 | Date & Time for Model - PR24CA88 | Text | Price Review 2024 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16
ANH | PR24QA_PR24CA88_OUT2 | Name of Model - PR24CA88 | Text | Price Review 2024 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
ANH | PR24QA_PR24CA88_OUT3 | F_Inputs time stamp - PR24CA88 | Text | Price Review 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ANH | PR24QA_PR24CA88_OUT4 | Model override switch for - PR24CA88 | nr | Price Review 2024 | 1 | bar: 2023-24 to 2029-30
ANH | C_PR24CA88_ENH_WW_ASSESSED | Total amount assessed - Wastewater - Net zero wastewater - Totex | £m | Price Review 2024 | 76.2058
HDD | C_PR24CA88_ENH_WW_TOT | Total enhancement allowance - Wastewater - Net zero wastewater - Totex | £m | Price Review 2024 |  |  |  | 0.49147 | 0.29561 | 0.025488 | 0.025488 | 0.025488
HDD | C_PR24CA88_ENH_WW_AP | Total enhancement allowance - Wastewater - Net zero wastewater - Accelerated programme | £m | Price Review 2024
HDD | C_PR24CA88_ENH_WW_TE | Total enhancement allowance - Wastewater - Net zero wastewater - Transition allowance | £m | Price Review 2024
HDD | PR24QA_PR24CA88_OUT1 | Date & Time for Model - PR24CA88 | Text | Price Review 2024 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16
HDD | PR24QA_PR24CA88_OUT2 | Name of Model - PR24CA88 | Text | Price Review 2024 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
HDD | PR24QA_PR24CA88_OUT3 | F_Inputs time stamp - PR24CA88 | Text | Price Review 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HDD | PR24QA_PR24CA88_OUT4 | Model override switch for - PR24CA88 | nr | Price Review 2024 | 1 | bar: 2023-24 to 2029-30
HDD | C_PR24CA88_ENH_WW_ASSESSED | Total amount assessed - Wastewater - Net zero wastewater - Totex | £m | Price Review 2024 | 0.86355
NES | C_PR24CA88_ENH_WW_TOT | Total enhancement allowance - Wastewater - Net zero wastewater - Totex | £m | Price Review 2024 |  |  |  | 0 | 0 | 0 | 0 | 0
NES | C_PR24CA88_ENH_WW_AP | Total enhancement allowance - Wastewater - Net zero wastewater - Accelerated programme | £m | Price Review 2024
NES | C_PR24CA88_ENH_WW_TE | Total enhancement allowance - Wastewater - Net zero wastewater - Transition allowance | £m | Price Review 2024
NES | PR24QA_PR24CA88_OUT1 | Date & Time for Model - PR24CA88 | Text | Price Review 2024 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16
NES | PR24QA_PR24CA88_OUT2 | Name of Model - PR24CA88 | Text | Price Review 2024 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
NES | PR24QA_PR24CA88_OUT3 | F_Inputs time stamp - PR24CA88 | Text | Price Review 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NES | PR24QA_PR24CA88_OUT4 | Model override switch for - PR24CA88 | nr | Price Review 2024 | 1 | bar: 2023-24 to 2029-30
NES | C_PR24CA88_ENH_WW_ASSESSED | Total amount assessed - Wastewater - Net zero wastewater - Totex | £m | Price Review 2024 | 0
NWT | C_PR24CA88_ENH_WW_TOT | Total enhancement allowance - Wastewater - Net zero wastewater - Totex | £m | Price Review 2024 |  |  |  | 27.7245 | 1.9547 | 1.8659 | 1.8153 | 1.7604
NWT | C_PR24CA88_ENH_WW_AP | Total enhancement allowance - Wastewater - Net zero wastewater - Accelerated programme | £m | Price Review 2024
NWT | C_PR24CA88_ENH_WW_TE | Total enhancement allowance - Wastewater - Net zero wastewater - Transition allowance | £m | Price Review 2024
NWT | PR24QA_PR24CA88_OUT1 | Date & Time for Model - PR24CA88 | Text | Price Review 2024 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16
NWT | PR24QA_PR24CA88_OUT2 | Name of Model - PR24CA88 | Text | Price Review 2024 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
NWT | PR24QA_PR24CA88_OUT3 | F_Inputs time stamp - PR24CA88 | Text | Price Review 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NWT | PR24QA_PR24CA88_OUT4 | Model override switch for - PR24CA88 | nr | Price Review 2024 | 1 | bar: 2023-24 to 2029-30
NWT | C_PR24CA88_ENH_WW_ASSESSED | Total amount assessed - Wastewater - Net zero wastewater - Totex | £m | Price Review 2024 | 42.1527
SRN | C_PR24CA88_ENH_WW_TOT | Total enhancement allowance - Wastewater - Net zero wastewater - Totex | £m | Price Review 2024 |  |  |  | 0 | 0 | 0 | 0 | 0
SRN | C_PR24CA88_ENH_WW_AP | Total enhancement allowance - Wastewater - Net zero wastewater - Accelerated programme | £m | Price Review 2024
SRN | C_PR24CA88_ENH_WW_TE | Total enhancement allowance - Wastewater - Net zero wastewater - Transition allowance | £m | Price Review 2024
SRN | PR24QA_PR24CA88_OUT1 | Date & Time for Model - PR24CA88 | Text | Price Review 2024 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16
SRN | PR24QA_PR24CA88_OUT2 | Name of Model - PR24CA88 | Text | Price Review 2024 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
SRN | PR24QA_PR24CA88_OUT3 | F_Inputs time stamp - PR24CA88 | Text | Price Review 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SRN | PR24QA_PR24CA88_OUT4 | Model override switch for - PR24CA88 | nr | Price Review 2024 | 1 | bar: 2023-24 to 2029-30
SRN | C_PR24CA88_ENH_WW_ASSESSED | Total amount assessed - Wastewater - Net zero wastewater - Totex | £m | Price Review 2024 | 0
SVE | C_PR24CA88_ENH_WW_TOT | Total enhancement allowance - Wastewater - Net zero wastewater - Totex | £m | Price Review 2024 |  |  |  | 41.486 | 72.711 | 56.038 | 60.89 | 63.81
SVE | C_PR24CA88_ENH_WW_AP | Total enhancement allowance - Wastewater - Net zero wastewater - Accelerated programme | £m | Price Review 2024
SVE | C_PR24CA88_ENH_WW_TE | Total enhancement allowance - Wastewater - Net zero wastewater - Transition allowance | £m | Price Review 2024
SVE | PR24QA_PR24CA88_OUT1 | Date & Time for Model - PR24CA88 | Text | Price Review 2024 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16
SVE | PR24QA_PR24CA88_OUT2 | Name of Model - PR24CA88 | Text | Price Review 2024 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
SVE | PR24QA_PR24CA88_OUT3 | F_Inputs time stamp - PR24CA88 | Text | Price Review 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SVE | PR24QA_PR24CA88_OUT4 | Model override switch for - PR24CA88 | nr | Price Review 2024 | 1 | bar: 2023-24 to 2029-30
SVE | C_PR24CA88_ENH_WW_ASSESSED | Total amount assessed - Wastewater - Net zero wastewater - Totex | £m | Price Review 2024 | 379.591
SWB | C_PR24CA88_ENH_WW_TOT | Total enhancement allowance - Wastewater - Net zero wastewater - Totex | £m | Price Review 2024 |  |  |  | 0 | 0 | 0 | 0 | 0
SWB | C_PR24CA88_ENH_WW_AP | Total enhancement allowance - Wastewater - Net zero wastewater - Accelerated programme | £m | Price Review 2024
SWB | C_PR24CA88_ENH_WW_TE | Total enhancement allowance - Wastewater - Net zero wastewater - Transition allowance | £m | Price Review 2024
SWB | PR24QA_PR24CA88_OUT1 | Date & Time for Model - PR24CA88 | Text | Price Review 2024 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16
SWB | PR24QA_PR24CA88_OUT2 | Name of Model - PR24CA88 | Text | Price Review 2024 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
SWB | PR24QA_PR24CA88_OUT3 | F_Inputs time stamp - PR24CA88 | Text | Price Review 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SWB | PR24QA_PR24CA88_OUT4 | Model override switch for - PR24CA88 | nr | Price Review 2024 | 1 | bar: 2023-24 to 2029-30
SWB | C_PR24CA88_ENH_WW_ASSESSED | Total amount assessed - Wastewater - Net zero wastewater - Totex | £m | Price Review 2024 | 0
TMS | C_PR24CA88_ENH_WW_TOT | Total enhancement allowance - Wastewater - Net zero wastewater - Totex | £m | Price Review 2024 |  |  |  | 0 | 0 | 0 | 0 | 0
TMS | C_PR24CA88_ENH_WW_AP | Total enhancement allowance - Wastewater - Net zero wastewater - Accelerated programme | £m | Price Review 2024
TMS | C_PR24CA88_ENH_WW_TE | Total enhancement allowance - Wastewater - Net zero wastewater - Transition allowance | £m | Price Review 2024
TMS | PR24QA_PR24CA88_OUT1 | Date & Time for Model - PR24CA88 | Text | Price Review 2024 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16
TMS | PR24QA_PR24CA88_OUT2 | Name of Model - PR24CA88 | Text | Price Review 2024 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
TMS | PR24QA_PR24CA88_OUT3 | F_Inputs time stamp - PR24CA88 | Text | Price Review 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TMS | PR24QA_PR24CA88_OUT4 | Model override switch for - PR24CA88 | nr | Price Review 2024 | 1 | bar: 2023-24 to 2029-30
TMS | C_PR24CA88_ENH_WW_ASSESSED | Total amount assessed - Wastewater - Net zero wastewater - Totex | £m | Price Review 2024 | 55.446
WSH | C_PR24CA88_ENH_WW_TOT | Total enhancement allowance - Wastewater - Net zero wastewater - Totex | £m | Price Review 2024 |  |  |  | 6.3079 | 7.2758 | 7.2641 | 7.3845 | 7.1256
WSH | C_PR24CA88_ENH_WW_AP | Total enhancement allowance - Wastewater - Net zero wastewater - Accelerated programme | £m | Price Review 2024
WSH | C_PR24CA88_ENH_WW_TE | Total enhancement allowance - Wastewater - Net zero wastewater - Transition allowance | £m | Price Review 2024
WSH | PR24QA_PR24CA88_OUT1 | Date & Time for Model - PR24CA88 | Text | Price Review 2024 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16
WSH | PR24QA_PR24CA88_OUT2 | Name of Model - PR24CA88 | Text | Price Review 2024 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
WSH | PR24QA_PR24CA88_OUT3 | F_Inputs time stamp - PR24CA88 | Text | Price Review 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WSH | PR24QA_PR24CA88_OUT4 | Model override switch for - PR24CA88 | nr | Price Review 2024 | 1 | bar: 2023-24 to 2029-30
WSH | C_PR24CA88_ENH_WW_ASSESSED | Total amount assessed - Wastewater - Net zero wastewater - Totex | £m | Price Review 2024 | 36.6287
WSX | C_PR24CA88_ENH_WW_TOT | Total enhancement allowance - Wastewater - Net zero wastewater - Totex | £m | Price Review 2024 |  |  |  | 0.74424 | 0.11752 | 0.91143 | 0.22339 | 0.2245
WSX | C_PR24CA88_ENH_WW_AP | Total enhancement allowance - Wastewater - Net zero wastewater - Accelerated programme | £m | Price Review 2024
WSX | C_PR24CA88_ENH_WW_TE | Total enhancement allowance - Wastewater - Net zero wastewater - Transition allowance | £m | Price Review 2024
WSX | PR24QA_PR24CA88_OUT1 | Date & Time for Model - PR24CA88 | Text | Price Review 2024 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16
WSX | PR24QA_PR24CA88_OUT2 | Name of Model - PR24CA88 | Text | Price Review 2024 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
WSX | PR24QA_PR24CA88_OUT3 | F_Inputs time stamp - PR24CA88 | Text | Price Review 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WSX | PR24QA_PR24CA88_OUT4 | Model override switch for - PR24CA88 | nr | Price Review 2024 | 1 | bar: 2023-24 to 2029-30
WSX | C_PR24CA88_ENH_WW_ASSESSED | Total amount assessed - Wastewater - Net zero wastewater - Totex | £m | Price Review 2024 | 11.8429
YKY | C_PR24CA88_ENH_WW_TOT | Total enhancement allowance - Wastewater - Net zero wastewater - Totex | £m | Price Review 2024 |  |  |  | 8.98 | 10.043 | 1.396 | 1.396 | 1.395
YKY | C_PR24CA88_ENH_WW_AP | Total enhancement allowance - Wastewater - Net zero wastewater - Accelerated programme | £m | Price Review 2024
YKY | C_PR24CA88_ENH_WW_TE | Total enhancement allowance - Wastewater - Net zero wastewater - Transition allowance | £m | Price Review 2024
YKY | PR24QA_PR24CA88_OUT1 | Date & Time for Model - PR24CA88 | Text | Price Review 2024 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16 | […]16/12/2024 14:53:16
YKY | PR24QA_PR24CA88_OUT2 | Name of Model - PR24CA88 | Text | Price Review 2024 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
YKY | PR24QA_PR24CA88_OUT3 | F_Inputs time stamp - PR24CA88 | Text | Price Review 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
YKY | PR24QA_PR24CA88_OUT4 | Model override switch for - PR24CA88 | nr | Price Review 2024 | 1 | bar: 2023-24 to 2029-30
YKY | C_PR24CA88_ENH_WW_ASSESSED | Total amount assessed - Wastewater - Net zero wastewater - Totex | £m | Price Review 2024 | 23.21